## Table of Contents
TRADE AGREEMENT AND ORDERS COST ANALYSIS
|  |  | Prepared Date: | 2011-12-28
TABLE OF CONTENTS
SECTION |  |  |  | Page
1 | SUMMARY |  |  | 1
2 | NOx CONTROL TECHNOLOGY OPTIONS AND COST OVERVIEW OF ACTIVE TA&O UNITS - Table 1 (General Table) |  |  | 2
3 | LIST OF 2010 ACTIVE TRADING AGREMENTS & ORDERS - Table 2 |  |  | 3
4 | EMISSION UNIT SPECIFICATIONS AND RECORD DATA |  |  | 4
5 | TA&O UNITS EPA CAIROS NOx EMISSIONS DATA (OZONE SEASON) - Table 3 |  |  | 5
6 | TA&O EMISSION UNITS NOx GRAPHS - Figures 1, 2, 3, 4, 5, 6, 7 and 8 |  |  | 6
7 | LIST OF NOx CONTROL TECHNOLOGIES / OPTIONS ASSESSSED BY EMMISSION UNIT OWNERS - Table 4 |  |  | 7
8 | TA&O UNITS OWNERS' COST ANALYSIS REPORTS SPECIFICATIONS - Table 5 |  |  | 8
9 | TOTAL CAPITAL COST ELEMENTS DEFINITION - Figure 9 |  |  | 9
10 | TOTAL ANNUAL COST ELEMENTS DEFINITION - Figure 10 |  |  | 10
11 | TA&O UNITS - PROPOSED NOx CONTROL TECHNOLOGIES EFFICENCY ASSESSMENT - Table 6 |  |  | 11
12 | EMISSION UNITS ID AND RECORD DATA - Table 7 |  |  | 12
13 | NOx CONTROL OPTIONS COST ANALYSIS - Table 8 |  |  | 13
ANNEX
1 | Unit CAIROS Emissions Report - Ozone Season |  |  | A1
2 | Major Equipment List for an SCR Application |  |  | A2

## 1(abs)
X
SUMMARY
To assist in the determination of how DEEP will proceed upon expiration on May 31, 2014 of the NOx Trading Agreement and Orders (TA&Os) issued to the owners of 39 electric generating units (EGUs), DEEP has reviewed the control costs and emissions data submitted by the unit owners.
Findings
The total ozone season NOx emissions from the 39 units were about 1,271 tons in 2008, 309 tons in 2009 and 1,167 tons in 2010. Despite relatively high emission rates, the total seasonal NOx emissions for the 39 units are low because most of the units operate for very few hours during the season. The exceptions to the low seasonal operating hours are Capital District and Bridgeport Harbor 3.
Submitted cost and emissions data resulted in control cost estimates that ranged from a low of 2,797 $/ton NOx reduced (flue gas recirculation at New Haven Harbor auxiliary boiler) to a high of 1,294,738 $/ton of NOx reduced (SCR and ID fans at Norwalk Harbor Station unit 1).
The owners submitted data and control cost estimates varied significantly in the assumptions and methods. We do not necessarily dispute the choice of methods or escalation of standard costs based on site-specific concerns. However, the variations limit the use of the submitted information. DEEP performed its own leveled cost analysis for the units to see if the result differed. The result of the evaluation – that controls are not cost effective – was unchanged.
Based on both the owner submitted control costs and emissions and DEEP’s leveled cost analysis using EPA data and comparable assumptions, the costs of controlling NOx emissions from the TA&O units is higher than control costs for NOx considered reasonable in permitting and attainment planning. The one exception is the auxiliary boiler at New Haven Harbor at which the installation of NOx controls and a change in fuel appear to be cost effective.
TAO OVERVIEW
| ● | Time period of NOx Trading Agreements & Orders: May 1, 2010 through May 31, 2014.
| ● | DEEP indicated to EGU owners that the use of trading as a compliance option would likely terminate with this set of TA&Os. The EGU owners would need to install controls, replace the existing units or shut down. This statement assumed that a number of federal rules impacting EGU's would have been published during term of TA&Os.
| ● | Eight TA&Os have been issued to six EGU owners:
|  | – | Capitol District Energy Center Cogeneration Associates |  |  |  |  | CDECCA
|  | – | Connecticut Resources Recovery Authority |  |  |  |  | CRRA
|  | – | FirstLight Hydro Generating Company |  |  |  |  | FirstLight
|  | – | Norwich Public Utilities |  |  |  |  | NPU
|  | – | NRG Energy, Inc |  |  |  |  | NRG
|  | – | PSEG Power LLC, PSEG Fossil LLC, PSEG Power Connecticut |  |  |  |  | PSEG
| ● | The eight TA&Os apply to 39 emission units
|  | – | Combustion Turbines |  |  | 27
|  |  |  | combustion-cycle |  | 1
|  |  |  | simple-cycle |  | 26
|  | – | Reciprocating Engines |  |  | 2
|  | – | Utility Boilers |  |  | 10
|  |  |  | load following boilers (LFBs) |  | 8
|  |  |  | facility auxiliary boiler |  | 1
|  |  |  | coal-fired boiler |  | 1
| ● | The TA&Os required EGU owners to submit in Spring 2011 an evaluation for every subject unit. Owners were instructed to include costs for all potential NOx control technologies available to limit emission below the limitations set by RCSA Section 22a-174-22 without the use of NOx allowances or DERCs.
Emissions
| ● | The total ozone season NOx emissions from the 39 units were about 1,271 tons in 2008, 309 tons in 2009 and 1,167 tons in 2010. For comparison, the entire state anthropogenic ozone season NOx emissions were 51,102 tons (2002 base year), of which 17% or 8,690 tons were emitted by stationary sources.
| ● | Figures 1 (turbines) and 5 (boilers) provide for each of the 39 units the 2008-2010 ozone season NOx emissions in tons and emissions rate (gm/MWh). Despite relatively high emissions rates, the seasonal NOx emissions are low because most of the units operate for very few hours during the season (Figures 3 and 4). The only exceptions to the low seasonal operating hours are Capital District and Bridgeport Harbor 3.
| ● | TA&O Emission Units NOx Graphs, on page 6, are based on Table 3 CAIROS data:
Figure 1 - "Ozone Season NOx Emissions & Emission Rate (3-year Average) for TA&O Turbines"
Figure 2 - "Ozone Season 2010, 2009 and 2008 NOx Emissions Rates for TA&O Turbines"
Figure 3 - "Number of Operating Hours During Ozone Season for TA&O Turbines"
Figure 4 - "Electric Generation during Ozone Season for TA&O Turbines"
Figure 5 - "Ozone Season NOx Emissions & Emissions Rate (3-year Average) for TA&O Boilers"
Figure 6 - "Ozone Season 2010, 2009 and 2008 NOx Emissions Rate for TA&O Boilers"
Figure 7 - "Number of Operating Hours During Ozone Season for TA&O Boilers"
Figure 8 - "Electric Generation During Ozone Season for TA&O Boilers"
Cost Analysis of Proposed NOx Control Technologies: Overview and Notes
| ● | For each identified control technology, the owner provided the cost of installing and operating the control; a schedule for installation and operation; feasibility, control performance assessment and any collateral environmental impacts that will result from the installation of additional controls.
| ● | Owners used several different approaches in calculating the cost effectiveness, so those values submitted are not directly comparable. The differences are caused largely by the choice of capital recovery interest rates and asset lifetime.
| ● | For each of the 39 units, three approaches were used to calculate the control cost, as follows:
Approach 1 – NOx Control Technologies, as provided by EGU owners
Approach 2 - NOx Control Technologies, based on:
EPA's CAIROS Ozone Season Data, NOx records max. of (2010, 2009, 2008)
Leveled Capital Recovery Factor
Unit Owners' Total capital Cost and Annual
Approach 3 - NOx Control Technologies , based on:
EPA's CAIROS Ozone Season Data, NOx records max. of (2010, 2009, 2008)
Leveled Capital Recovery Factor
Controls Cost following EPA's guidelines. Some controls cost assessed per EPA's formulas, if available (HPWI and SCR for turbines, only) and per EGU's owner data. All costs' base year is 2011
The values calculated using all three approaches are set out in Table 1.
| ● | In general, all unit owners indicate that the emission units' sites are congested. The cost of installing NOx controls may increase due to site preparation, interference with the existing (high voltage) power lines and other existing utilities (water lines, tanks, etc.) that have to be removed or relocated. Some reports included (high) costs for equipment erection, construction contracts, testing and start-up and permitting.
| ● | For example, NRG reported for all utility boilers:
|  | – | A ratio SCR vs. Equipment Erection Cost of 1: 1.3 to 1.8 times; the highest costs assigned for two of NRG facilities (Middletown 4 and Montville 5) are $38 mil for equipment erection vs. $28 mil for SCR procurement, with a total capital cost reported for each of these facilities of $145 mil; NOx removal cost effectiveness resulted $984,549.
|  | – | Other high cost items had been added such as construction contracts and contractor's fees, foundations, repairing the existing stacks, testing costs and numerous additional owners' costs.
|  | – | Also the NRG report considered only 5 years and a higher annual interest 9% for estimating the Capital Recovery factor, and that along with a higher capital cost leading to a very high NOx control cost effectiveness.
| ● | In developing the cost analysis reports, units’ owners referred to two EPA's cost guidance documents but changed the cost items' factors, added new costs, and used higher multipliers than recommended by EPA. Among the reasons cited for the diversion from EPA's guidance were the site specifics and historic data (similar projects from the past).
| ● | EPA documents quoted as references are as follows:
|  | 1 | EPA OAQPS Control Cost Manual, Sixth Edition EPA-452-02-001, January 2002
Document is not completed yet. "Section 4 - NOx Controls, Chapter 3- Steam /Water Injection" is a "Planned Chapter".
All costs base year is 1998
NOx Controls Total Capital Cost (TCC) and Total Annual Cost (TAC) are well defined, however method indicated is laborious.
|  | 2 | EPA - Alternative Control Techniques Document - NOx Emissions from Stationary Gas Turbines, January 1993
Refer to NOx controls applied to combustion turbines only
All costs base year is 1993
TA&O units models are either not listed or listed with a different make
Document defines thoroughly cost items elements of TCC for Water Injection and SCR controls of several existing facilities allowing a capital cost bulk estimate, considered acceptable.
| ● | Per EPA, an existing equipment retrofitting may significantly increase the costs (60 % or more) depending on the site specifics. Also the recommended costs do not include construction of a new building or site preparation costs.
| ● | Using the leveled cost analysis approach based on EPA guidelines and data recalculated with comparable assumptions, the result was the same: the cost of control for the TA&O units is far higher than control costs for NOx considered reasonable to date.
GUIDE TO THE TABLES, FORMS AND FIGURES
| ● | Table 1 - "NOx Control Technology Options and Cost Overview of 2010 Active TA&O Units", on page 2, summarizes the cost analysis results. Table 1 provides each control option proposed for every emission unit and three cost metrics for each option: the capital cost, the capital cost adjusted for unit capacity ($/MW) and the control cost effectiveness ($/tons of NOx reduced. Table 1 also includes for each option per unit the NOx control efficiency, NOx rate estimate and estimated tons/year NOx reduction.
(Note: Table 1 provides the option to select the NOx rate either in "lb/MMBtu" or in "ppmvd". Due to missing conversion factor, ppmvd fields may be blank. Also in Section II and III the Capital Recovery Factor (CRF) may be changed by selecting new values of the asset life and annual interest for each group emission units (turbines/diesel engines and/or utility boilers).
| ● | Table 2 - "List of 2010 Active Trading Agreements & Orders", on page 3, includes the emission units. specifications (tag ID, nominal capacity, equipment age and primary and secondary fuel) subject to 2010 active TA&Os.
Form on page 4 - "Emission Unit Specifications and Record Data", allows seeing the record data, as provided by EGU's owners, of every unit listed within 2010 active TA&Os.
(Note: Click on any list no's located on Table 3 left side to open record' form and select from the drop down list the unit list no. to display the record)
| ● | Table 3 - "TA&O Units EPA CAIROS NOx Emission Data (Ozone Season)", on page 5, indicates the 2010, 2009 and 2008 NOx data, including the reported operating time, gross load, average NOx rate and tons/year, heat input, and the primary and secondary fuels. Original record data, imported from EPA CAIROS is included in Annex 1. Table 3 indicates the maximum of the 2010, 2009 and 2008 NOx emissions in tons per year, data that served for the cost analysis summarized in Sections II and III of Table1. (Note: See Table 3, Columns 95 through 102).
| ● | Table 4 - "List of NOx Control Technologies / Options Assessed by Emission Units Owners", on page 7, includes all the NOx control options considered and analyzed in the reports submitted by the EGU's owners for the facilities subject to the 2010 Trading Agreements and Orders. Table 4 data is as provided by the owners' reports. Table 4 includes a short description of the listed NOx Control Technologies, owners' reports efficiency assessment, equipment availability, and owners' remarks on site condition and existing utilities.
(Note: Not all data provided have been included. Additional information should be found in the reports submitted by the EGU owners. Also, due to the tabular format some fields may not display the entire content. However the complete information is shown in the facility record in the form on page 3.)
| ● | Table 5 - "TA&O Units Owners' Cost Analysis Reports Specifications", on page 8, summarizes differences among the owners' reports.
Figure 9 - "Total Capital Cost Elements Definition", on page 9, shows EPA's graphical representation from ref. # 1, EPA-452-02-001. Cost items terms found in TA&O owners reports were added under the appropriate EPA class. TCC schematic and percentage factors, recommended by EPA/452/B-02-001 were used to perform a leveled cost analysis for the 2010 active Trading Agreements and Orders, results shown in Section III of Table 1.
Figure 10 - "Total Annual Cost Elements Definition" on page 10, is the EPA's graphical representation from ref. # 1, EPA-452-02-001. TAC schematic and the methods detailed in page 10 for Water Injection and SCR were used to perform a leveled cost analysis for the 2010 active Trading Agreements and Orders, results shown in Section III of Table 1.
| ● | Table 6 - "TA&O Units - Proposed NOx Control Technologies Efficiency Assessment", on page 11, included proposed controls efficiencies. Also allows efficiency re-calculation and assessment if a change is required. For instance, for a legitimate cost effectiveness comparison all SCR controls should have assigned same efficiency (of 90%) or all water injection should have 60%. Last columns of Table 6 show both owners report proposed controls efficiencies as well as the assigned efficiencies to perform a leveled cost analysis.
| ● | Table 7 - "Emission Units ID and Record Data", on page 12, is the data entry table for emission units ID records and specifications (input data) from DEEP documents and unit owners' reports.
| ● | Table 8 - "NOx Control Options Cost Analysis", on page 13, includes:
|  |  | Section I |  | Owners' cost analysis data and controls cost effectiveness, as reported
|  |  | Section II |  | Re-calculation of the same data based on EPA CAIROS Ozone Season NOx records, also fixing reports calculation errors
|  |  | Section III |  | A leveled cost analysis of all controls based on EPA CAIROS Ozone Season NOx records, an uniform CRF and EPA's recommended cost assessment.
| ● | For some controls such an SCR, EPA published detailed lists of that control required components, see Annex 2. For other components such information may be found within manufacturers' product description.
*
[6 empty] | * | *

## 2(gnl)
Summary:
– Table 1 includes the 2010 Active Trade Agreements & Orders (TA&O) Cost Analysis three approaches results shown in Section I, II and III, respectively.
– Assessment criteria of each method is listed beneath the appropriate section title.
– Fields marked in light green allow data entry (click on the cell drop down right arrow to select a new value):
- Capital Recovery Factor input data ( Equipment Life & Interest)
- NOx Rate units may be selected either lb/MMBtu or ppmvd. Due to missing conversion factor, ppmvd fields may be blank.
x
[7 empty] | NOx CONTROL TECHNOLOGY OPTIONS AND COST OVERVIEW OF ACTIVE TA&O UNITS | [6 empty] | DATA ARRANGEMENT AND RECORD DESCRIPTION | [8 empty] | SECTION II- CAPITAL RECOVERY FACTOR |  |  |  |  | SECTION III - CAPITAL RECOVERY FACTOR
[14 empty] | Option No. |  | NOx Control Technology Option Name |  |  |  |  | TURBINES & DIESEL ENG. - CRF |  |  |  |  | TURBINES & DIESEL ENG. - CRF
[16 empty] | NOx Control Efficiency , η % | Controlled NOx Rate, in lb/MMBtu / ppmvd | NOx (R) reduction, in ton/yr |  |  | n | 20 |  |  |  | n | 25
[8 empty] | SECTION I | Summary of Unit Owners's Assessment Data as reported | [11 empty] | i% | 7% |  |  |  | i% | 7%
[8 empty] | SECTION II | Cost Analysis based on EPA CAIROS NOx Data and Unit Owners' costs, corrected following reports' methodology and applying a uniform Capital Recovery Factor (CRF) | [6 empty] | Total Capital Cost of NOx Control Technology - $TCC/unit |  | Capital Recovery (CR) - $/yr |  |  | CRF | 0.094393 |  |  |  | CRF | 0.085811
[16 empty] | Total Capital Cost (TCC) / MW nominal capacity - Ratio |  |  |  |  | UTILITY BOILERS - CRF |  |  |  |  | UTILITY BOILERS - CRF
[8 empty] | SECTION III | Cost Analysis based on EPA CAIROS NOx Data and Reports Costs following EPA's guidelines. Some controls costs assessed per EPA formulas, if available (HPWI and SCR for turbines, only) | [11 empty] | n | 40 |  |  |  | n | 40
[16 empty] | Cost Effectiveness - $/ton NOx reduced - based on Annual Operation Costs and Capital Recovery |  |  |  |  | i% | 7% |  |  |  | i% | 7%
[21 empty] | CRF | 0.075009 |  |  |  | CRF | 0.075009
Table 1
[5 empty] | No. | Owner / Operator | TAO | Premises / Facility Name | ID | Nom. Power | Age | Existing NOx Controls | Fuel (s) | NOx CONTROL TECHNOLOGY ECONOMIC ANALYSIS
[14 empty] | Option No. | SECTION I |  |  |  | SECTION II |  |  |  |  | SECTION III
[15 empty] | NOx Control Technology Emmission Units Owners' Economic Analysis |  |  |  | NOx Control Technology - Economic Analysis based on CAIROS Data and Stakeholders' Costs |  |  |  |  | NOx Control Technology - Economic Analysis based on CAIROS Data and EPA's Approach
[16 empty] | - Units Owners' Reports NOx Assessment Data - Capital Recovery Factor, as selected in reports - Unit Owners' Total Capital and Annual Cost Estimates |  |  |  | - CAIROS Data (ozone season) max of 2010, 2009, 2008 - Leveled Capital Recovery Factor - Unit Owners' Total Capital & Annual Costs (corrected) |  |  |  |  | - CAIROS Data (ozone season) max of 2010, 2009, 2008 - Leveled Capital Recovery Factor - Total Capital per EPA Approach and Unit Owners' Reports Annual Costs per EPA Approach - all costs' base year 2011
[5 empty] | 1 |  | 2 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 |  |  |  | 12 |  |  |  |  | 13
TURBINES
| REFERENCE ID | [5 empty] | 2: Capitol District Energy Center Cogeneration Associates
8298-01 | CDECCA | GT | 8298-01-01 |  | 1 | Capitol District Energy Center Cogeneration Associates | 2: 8298; 4: Capitol District Energy Center; 5: GT; 7: 38 yrs; 9: Natural Gas; No. 2 oil | Unit Owner report not provided |  |  |  | not assessed - missing unit owner report |  |  |  |  | not assessed - unit owner report and data not provided
[25 empty] | Note: | Section III, Turbines' HPWI and SCR - TCC based on EPA1993 ACT re: 2011
Connecticut Resources Recovery Authority
8302-01 | CRRA | 11A | 8302-01-01 |  | 2 | Connecticut Resources Recovery Authority | 8302 | South Meadow Station | 11A | 40 | 57 yrs | None | Jet Fuel A (Kerosene K1); No. 2 oil | 1 |  | Selective Catalytic Reduction (SCR) |  |  |  | Selective Catalytic Reduction (SCR) |  |  |  |  | Selective Catalytic Reduction (SCR)
|  | #VALUE! |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | #VALUE! |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | η ≈ 90% |  | 1.2 |  | η ≈ 90% | 0.079 lb/MMBtu | 1.4 |  |  | η ≈ 90% | 0.079 lb/MMBtu | 1.4
8302-02 |  | 11B |  |  | 3 |  | 8302 | South Meadow Station | 11B |  | 57 yrs | None | Jet Fuel A (Kerosene K1); No. 2 oil
|  | #VALUE! |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 2283347 | $ TCC/unit | 537499.8838 |  | 2102390 | $ TCC/unit | 198450.7432 |  |  | 2513690 | $ TCC/unit | 215701.039
|  | #VALUE! |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 114167.35 | $ TCC/MW nom |  |  | 105119.5 | $ TCC / MW nominal capacity |  |  |  | 125684.5 | $ TCC / MW nominal capacity
8302-03 |  | 12A |  |  | 4 |  | 8302 | South Meadow Station | 12A | 40 | 57 yrs | None | Jet Fuel A (Kerosene K1); No. 2 oil |  |  | 485192.3613 | $ /ton NOx(R) |  |  | 162478.9764 | $ /ton NOx(R) |  |  |  | 241075.3475 | $ /ton NOx(R)
|  | #VALUE! |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | #VALUE! | 8302-01-02 |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2 |  | HPWI + Ultra Low Sulfur Fuel |  |  |  | HPWI + Ultra Low Sulfur Fuel |  |  |  |  | HPWI + Ultra Low Sulfur Fuel
8302-04 |  | 12B |  |  | 5 |  | 8302 | South Meadow Station | 12B |  | 57 yrs | None | Jet Fuel A (Kerosene K1); No. 2 oil |  |  | (Water Injection w/ Low Sulfur Fuel Combination) |  |  |  | (Water Injection w/ Low Sulfur Fuel Combination) |  |  |  |  | (Water Injection w/ Low Sulfur Fuel Combination)
|  | #VALUE! |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | η ≈ 75% |  | 1 |  | η ≈ 75% | 0.196 lb/MMBtu | 1.1 |  |  | η ≈ 75% | 0.196 lb/MMBtu | 1.1
|  | #VALUE! |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
8302-05 |  | 13A |  |  | 6 |  | 8302 | South Meadow Station | 13A | 40 | 57 yrs | None | Jet Fuel A (Kerosene K1); No. 2 oil |  |  | 1494237.5 | $ TCC/unit | 351743.5075 |  | 1494237.5 | $ TCC/unit | 141045.4494 |  |  | 1738175 | $ TCC/unit | 149153.6958
|  | #VALUE! |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 74711.875 | $ TCC / MW nominal capacity |  |  | 74711.875 | $ TCC / MW nominal capacity |  |  |  | 86908.75 | $ TCC / MW nominal capacity
|  | #VALUE! |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 525243.3086 | $ /ton NOx(R) |  |  | 148042.7328 | $ /ton NOx(R) |  |  |  | 197937.3583 | $ /ton NOx(R)
8302-06 |  | 13B |  |  | 7 |  | 8302 | South Meadow Station | 13B |  | 57 yrs | None | Jet Fuel A (Kerosene K1); No. 2 oil
|  | #VALUE! | 8302-01-03 |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3 |  | High Pressure Water Injection (HPWI) |  |  |  | High Pressure Water Injection (HPWI) |  |  |  |  | High Pressure Water Injection (HPWI)
|  | #VALUE! |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
8302-07 |  | 14A |  |  | 8 |  | 8302 | South Meadow Station | 14A | 40 | 57 yrs | None | Jet Fuel A (Kerosene K1); No. 2 oil |  |  | η ≈ 60% |  | 0.8 |  | η ≈ 60% | 0.314 lb/MMBtu | 0.9 |  |  | η ≈ 60% | 0.314 lb/MMBtu | 0.9
|  | #VALUE! |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | #VALUE! |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 1481737.5 | $ TCC/unit | 348801.0075 |  | 1481737.5 | $ TCC/unit | 139865.5378 |  |  | 1725675 | $ TCC/unit | 148081.0643
8302-08 |  | 14B |  |  | 9 |  | 8302 | South Meadow Station | 14B |  | 57 yrs | None | Jet Fuel A (Kerosene K1); No. 2 oil |  |  | 74086.875 | $ TCC / MW nominal capacity |  |  | 74086.875 | $ TCC / MW nominal capacity |  |  |  | 86283.75 | $ TCC / MW nominal capacity
|  | #VALUE! |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 474907.3086 | $ /ton NOx(R) |  |  | 172707.9587 | $ /ton NOx(R) |  |  |  | 245672.7462 | $ /ton NOx(R)
|  | #VALUE! |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[7 empty] | 2: Note: | Unit NOx Rate - | lb/MMBtu |  |  | Unit NOx Rate - | lb/MMBtu |  |  |  | Unit NOx Rate - | lb/MMBtu
[7 empty] | 2: TCC cost shown is per unit. Since each of the South Meadows units is a twin pack, the actual TCC of a twin pack control is double the value indicated in the table. | [9 empty] | Note:
Some Section III, Cost Effectiveness Indicators may be higher vs. Section II, due using a leveled Total Annual Direct Costs for all TA&O units based on reports available data (esp. NRG)
[16 empty] | Note: | TCC of New Equipment (option 7 and 8) has lower values in Section I & II since the capital cost was adjusted with salvage value and loss revenue. Section III shows TCC before adjustment | [7 empty] | Note: | Section III, Turbines' HPWI and SCR - TCC based on EPA1993 ACT re: 2011
TURBINES
FirstLight Hydro Generating Company
8303-01 | FirstLight | 10 | 8303-01-01 |  | 10 | FirstLight Hydro Generating Company | 8303 | Tunnel | 10 | 20 | 58 yrs | None | Jet Fuel A (Kerosene K1); | 1 |  | SCR + HPWI + CO Catalyst + Dual Fuel |  |  |  | SCR + HPWI + CO Catalyst + Dual Fuel |  |  |  |  | SCR + HPWI + CO Catalyst + Dual Fuel
[7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | (Natural Gas with Oil backup) |  |  |  | (Natural Gas with Oil backup) |  |  |  |  | (Natural Gas with Oil backup)
[7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | η ≈ 97% | 5 ppmvd | 4.5 |  | η ≈ 97% | 0.020 lb/MMBtu | 1.7 |  |  | η ≈ 97% | 0.020 lb/MMBtu | 1.7
[7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 6310000 | $ TCC/unit | 595619 |  | 6310000 | $ TCC/unit | 595619.3614 |  |  | 6939365 | $ TCC/unit | 595470.4998
[7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 315500 | $ TCC / MW nominal capacity |  |  | 315500 | $ TCC / MW nominal capacity |  |  |  | 346968.25 | $ TCC / MW nominal capacity
[7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 190292 | $ /ton NOx(R) |  |  | 512561.2593 | $ /ton NOx(R) |  |  |  | 535953.4608 | $ /ton NOx(R)
|  |  | 8303-01-02 |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2 |  | SCR + HPWI + CO Catalyst |  |  |  | SCR + HPWI + CO Catalyst |  |  |  |  | SCR + HPWI + CO Catalyst
[7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | (Primary fuel Oil - Kerosene K1) |  |  |  | (Primary fuel Oil - Kerosene K1) |  |  |  |  | (Primary fuel Oil - Kerosene K1)
[7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | η ≈ 95% | 10 ppmvd | 4.3 |  | η ≈ 95% | 0.040 lb/MMBtu | 1.6 |  |  | η ≈ 95% | 0.040 lb/MMBtu | 1.6
[7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 3630000 | $ TCC/unit | 342646 |  | 3630000 | $ TCC/unit | 342646.3204 |  |  | 4439365 | $ TCC/unit | 380944.2068
[7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 181500 | $ TCC / MW nominal capacity |  |  | 181500 | $ TCC / MW nominal capacity |  |  |  | 221968.25 | $ TCC / MW nominal capacity
[7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 112635 | $ /ton NOx(R) |  |  | 303208.196 | $ /ton NOx(R) |  |  |  | 355416.9415 | $ /ton NOx(R)
|  |  | 8303-01-03 |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3 |  | Selective Catalytic Reduction (SCR) |  |  |  | Selective Catalytic Reduction (SCR) |  |  |  |  | Selective Catalytic Reduction (SCR)
[7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | (Primary fuel Oil - Kerosene K1) |  |  |  | (Primary fuel Oil - Kerosene K1) |  |  |  |  | (Primary fuel Oil - Kerosene K1)
[7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | η ≈ 87% | 25 ppmvd | 4 |  | η ≈ 87% | 0.100 lb/MMBtu | 1.5 |  |  | η ≈ 87% | 0.100 lb/MMBtu | 1.5
[7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 2730000 | $ TCC/unit | 257693 |  | 2730000 | $ TCC/unit | 257692.6873 |  |  | 2513690 | $ TCC/unit | 215701.039
[7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 136500 | $ TCC / MW nominal capacity |  |  | 136500 | $ TCC / MW nominal capacity |  |  |  | 125684.5 | $ TCC / MW nominal capacity
[7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 92753 | $ /ton NOx(R) |  |  | 249184.9752 | $ /ton NOx(R) |  |  |  | 221307.7771 | $ /ton NOx(R)
|  |  | 8303-01-04 |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4 |  | HPWI with Cookie Cutter Air Deflectors |  |  |  | HPWI with Cookie Cutter Air Deflectors |  |  |  |  | HPWI with Cookie Cutter Air Deflectors
[7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | (Primary fuel Oil - Kerosene K1) |  |  |  | (Primary fuel Oil - Kerosene K1) |  |  |  |  | (Primary fuel Oil - Kerosene K1)
[7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | η ≈ 73% | 50 ppmvd | 3.4 |  | η ≈ 73% | 0.199 lb/MMBtu | 1.2 |  |  | η ≈ 73% | 0.199 lb/MMBtu | 1.2
[7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 1005000 | $ TCC/unit | 94865 |  | 1005000 | $ TCC/unit | 94864.8904 |  |  | 1850675 | $ TCC/unit | 158807.379
[7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 50250 | $ TCC / MW nominal capacity |  |  | 50250 | $ TCC / MW nominal capacity |  |  |  | 92533.75 | $ TCC / MW nominal capacity
[7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 40565 | $ /ton NOx(R) |  |  | 108508.3725 | $ /ton NOx(R) |  |  |  | 190475.2318 | $ /ton NOx(R)
|  |  | 8303-01-05 |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5 |  | High Pressure Water Injection (HPWI) - Oil Kerosene K1 |  |  |  | High Pressure Water Injection (HPWI) - Oil Kerosene K1 |  |  |  |  | High Pressure Water Injection (HPWI) - Oil Kerosene K1
[7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | η ≈ 60% | 75 ppmvd | 2.7 |  | η ≈ 60% | 0.299 lb/MMBtu | 1 |  |  | η ≈ 60% | 0.299 lb/MMBtu | 1
[7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 880000 | $ TCC/unit | 83066 |  | 880000 | $ TCC/unit | 83065.7747 |  |  | 1725675 | $ TCC/unit | 148081.0643
[7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 44000 | $ TCC / MW nominal capacity |  |  | 44000 | $ TCC / MW nominal capacity |  |  |  | 86283.75 | $ TCC / MW nominal capacity
[7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 43744 | $ /ton NOx(R) |  |  | 116276.0048 | $ /ton NOx(R) |  |  |  | 217627.0033 | $ /ton NOx(R)
|  |  | 8303-01-06 |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 6 |  | Dual Fuel (Natural Gas with Liquid Backup) |  |  |  | Dual Fuel (Natural Gas with Liquid Backup) |  |  |  |  | Dual Fuel (Natural Gas with Liquid Backup)
[7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | η ≈ 36% | 120 ppmvd | 1.6 |  | η ≈ 36% | 0.478 lb/MMBtu | 0.6 |  |  | η ≈ 36% | 0.478 lb/MMBtu | 0.6
[7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 2860000 | $ TCC/unit | 269964 |  | 2860000 | $ TCC/unit | 269963.7676 |  |  | 2500000 | $ TCC/unit | 214526.2931
[7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 143000 | $ TCC / MW nominal capacity |  |  | 143000 | $ TCC / MW nominal capacity |  |  |  | 125000 | $ TCC / MW nominal capacity
[7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 234808 | $ /ton NOx(R) |  |  | 632822.6082 | $ /ton NOx(R) |  |  |  | 524979.9309 | $ /ton NOx(R)
|  |  | 8303-01-07 |  |  |  | 8: #N/A; 10: 7 | LM2500 DLE - new gas fired GE turbine |  |  |  | LM2500 DLE - new gas fired GE turbine |  |  |  |  | LM2500 DLE - new gas fired GE turbine
[7 empty] | 8: #N/A | η ≈ 87% | 25 ppmvd | 4 |  | η ≈ 87% | 0.100 lb/MMBtu | 1.5 |  |  | η ≈ 87% | 0.100 lb/MMBtu | 1.5
[7 empty] | 8: #N/A | 12360000 | $ TCC/unit | 1166697 |  | 12360000 | $ TCC/unit | 1166696.5622 |  |  | 13500000 | $ TCC/unit | 1158441.9825
[7 empty] | 8: #N/A | 618000 | $ TCC / MW nominal capacity |  |  | 618000 | $ TCC / MW nominal capacity |  |  |  | 675000 | $ TCC / MW nominal capacity
[7 empty] | 8: #N/A | 418610 | $ /ton NOx(R) |  |  | 1128178.1295 | $ /ton NOx(R) |  |  |  | 1160956.7284 | $ /ton NOx(R)
|  |  | 8303-01-08 |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 8 |  | LM2500 - new oil fired GE turbine |  |  |  | LM2500 - new oil fired GE turbine |  |  |  |  | LM2500 - new oil fired GE turbine
[7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | η ≈ 78% | 42 ppmvd | 3.6 |  | η ≈ 78% | 0.167 lb/MMBtu | 1.3 |  |  | η ≈ 78% | 0.167 lb/MMBtu | 1.3
[7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 10860000 | $ TCC/unit | 1025107 |  | 10860000 | $ TCC/unit | 1025107.1736 |  |  | 12000000 | $ TCC/unit | 1029726.2066
[7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 543000 | $ TCC / MW nominal capacity |  |  | 543000 | $ TCC / MW nominal capacity |  |  |  | 600000 | $ TCC / MW nominal capacity
[7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 411017 | $ /ton NOx(R) |  |  | 1107715.5601 | $ /ton NOx(R) |  |  |  | 1153856.7279 | $ /ton NOx(R)
[16 empty] | Unit NOx Rate - | ppmvd |  |  | Unit NOx Rate - | lb/MMBtu |  |  |  | Unit NOx Rate - | lb/MMBtu
[7 empty] | 2: TURBINES | Note: | TCC of New Equipment (option 7 and 8) has lower values in Section I & II since the capital cost was adjusted with salvage value and loss revenue. Section III shows TCC before adjustment | [7 empty] | Note: | Section III, Turbines' HPWI and SCR - TCC based on EPA1993 ACT re: 2011
Norwich Public Utilities
8304-01 | NPU | TRBINE | 8304-01-01 |  | 11 | Norwich Public Utilities | 8304 | Norwich | TRBINE | 18.8 | 55 yrs | None | No. 2 oil; | 1 |  | SCR + HPWI + Dual Fuel (Nat Gas - oil backup) |  |  |  | SCR + HPWI + Dual Fuel (Nat Gas - oil backup) |  |  |  |  | SCR + HPWI + Dual Fuel (Nat Gas - oil backup)
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | η ≈ 96% | 0.023 lb/MMBtu | 2.6 |  | η ≈ 96% | 0.026 lb/MMBtu | 1.4 |  |  | η ≈ 96% | 0.026 lb/MMBtu | 1.4
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 7319263.414 | $ TCC/unit | 690887 |  | 7319263.414 | $ TCC/unit | 690886.6879 |  |  | 6827843.836 | $ TCC/unit | 585900.8111
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 389322.522 | $ TCC / MW nominal capacity |  |  | 389322.522 | $ TCC / MW nominal capacity |  |  |  | 363183.1828 | $ TCC / MW nominal capacity
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 347672 | $ /ton NOx(R) |  |  | 684850.1091 | $ /ton NOx(R) |  |  |  | 606956.2377 | $ /ton NOx(R)
|  |  | 8304-01-02 |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2 |  | SCR + Water Injection (HPWI) - oil # 2 |  |  |  | SCR + Water Injection (HPWI) - oil # 2 |  |  |  |  | SCR + Water Injection (HPWI) - oil # 2
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | η ≈ 94% | 0.035 lb/MMBtu | 2.6 |  | η ≈ 94% | 0.040 lb/MMBtu | 1.4 |  |  | η ≈ 94% | 0.040 lb/MMBtu | 1.4
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 4554324.578 | $ TCC/unit | 429896 |  | 4554324.578 | $ TCC/unit | 429896.0217 |  |  | 4062905 | $ TCC/unit | 348639.9795
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 242251.3073 | $ TCC / MW nominal capacity |  |  | 242251.3073 | $ TCC / MW nominal capacity |  |  |  | 216111.9681 | $ TCC / MW nominal capacity
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 221348 | $ /ton NOx(R) |  |  | 435802.1368 | $ /ton NOx(R) |  |  |  | 372790.0691 | $ /ton NOx(R)
|  |  | 8304-01-03 |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3 |  | Selective Catalytic Reduction (SCR) |  |  |  | Selective Catalytic Reduction (SCR) |  |  |  |  | Selective Catalytic Reduction (SCR)
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | (Primary fuel No. 2 oil) |  |  |  | (Primary fuel No. 2 oil) |  |  |  |  | (Primary fuel No. 2 oil)
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | η ≈ 82% | 0.098 lb/MMBtu | 2.3 |  | η ≈ 90% | 0.062 lb/MMBtu | 1.4 |  |  | η ≈ 90% | 0.062 lb/MMBtu | 1.4
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 3386772.996 | $ TCC/unit | 319687 |  | 3386772.996 | $ TCC/unit | 319687.4119 |  |  | 2410512.8 | $ TCC/unit | 206847.3501
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 180147.4998 | $ TCC / MW nominal capacity |  |  | 180147.4998 | $ TCC / MW nominal capacity |  |  |  | 128218.766 | $ TCC / MW nominal capacity
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 187812 | $ /ton NOx(R) |  |  | 337154.3198 | $ /ton NOx(R) |  |  |  | 231294.9642 | $ /ton NOx(R)
|  |  | 8304-01-04 |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4 |  | High Pressure Water Injection (HPWI) |  |  |  | High Pressure Water Injection (HPWI) |  |  |  |  | High Pressure Water Injection (HPWI)
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | (Natural Gas with Oil backup) |  |  |  | (Natural Gas with Oil backup) |  |  |  |  | (Natural Gas with Oil backup)
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | η ≈ 67% | 0.184 lb/MMBtu | 1.8 |  | η ≈ 67% | 0.207 lb/MMBtu | 1 |  |  | η ≈ 67% | 0.207 lb/MMBtu | 1
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 1191551.582 | $ TCC/unit | 112474 |  | 1191551.582 | $ TCC/unit | 112474.04 |  |  | 1652392.2 | $ TCC/unit | 141792.6293
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 63380.4033 | $ TCC / MW nominal capacity |  |  | 63380.4033 | $ TCC / MW nominal capacity |  |  |  | 87893.2021 | $ TCC / MW nominal capacity
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 81969 | $ /ton NOx(R) |  |  | 159960.6458 | $ /ton NOx(R) |  |  |  | 211708.2072 | $ /ton NOx(R)
|  |  | 8304-01-05 |  |  |  | 8: #N/A; 10: 5 | Dual Fuel (Natural Gas with Liquid Backup) |  |  |  | Dual Fuel (Natural Gas with Liquid Backup) |  |  |  |  | Dual Fuel (Natural Gas with Liquid Backup)
[7 empty] | 8: #N/A | (Natural Gas with Oil backup) |  |  |  | (Natural Gas with Oil backup) |  |  |  |  | (Natural Gas with Oil backup)
[7 empty] | 8: #N/A | η ≈ 36% | 0.352 lb/MMBtu | 1 |  | η ≈ 36% | 0.397 lb/MMBtu | 0.5 |  |  | η ≈ 36% | 0.397 lb/MMBtu | 0.5
[7 empty] | 8: #N/A | 2908938.836 | $ TCC/unit | 274583 |  | 2908938.836 | $ TCC/unit | 274583.2475 |  |  | 2764938.836 | $ TCC/unit | 237260.8316
[7 empty] | 8: #N/A | 154730.7891 | $ TCC / MW nominal capacity |  |  | 154730.7891 | $ TCC / MW nominal capacity |  |  |  | 147071.2147 | $ TCC / MW nominal capacity
[7 empty] | 8: #N/A | 364103 | $ /ton NOx(R) |  |  | 717778.7902 | $ /ton NOx(R) |  |  |  | 646350.8633 | $ /ton NOx(R)
|  |  | 8304-01-06 |  |  |  | 8: #N/A; 10: 6 | Solar Titan 130 - new dual fuel w/ SoLoNOx |  |  |  | Solar Titan 130 - new dual fuel w/ SoLoNOx |  |  |  |  | Solar Titan 130 - new dual fuel w/ SoLoNOx
[7 empty] | 8: #N/A | (Natural Gas with Oil backup) |  |  |  | (Natural Gas with Oil backup) |  |  |  |  | (Natural Gas with Oil backup)
[7 empty] | 8: #N/A | η ≈ 89% | 0.059 lb/MMBtu | 2.4 |  | η ≈ 89% | 0.066 lb/MMBtu | 1.3 |  |  | η ≈ 89% | 0.066 lb/MMBtu | 1.3
[7 empty] | 8: #N/A | 13622600 | $ TCC/unit | 1285877 |  | 13622600 | $ TCC/unit | 1285877.0702 |  |  | 14834600 | $ TCC/unit | 1272964.6988
[7 empty] | 8: #N/A | 724606.383 | $ TCC / MW nominal capacity |  |  | 724606.383 | $ TCC / MW nominal capacity |  |  |  | 789074.4681 | $ TCC / MW nominal capacity
[7 empty] | 8: #N/A | 692571 | $ /ton NOx(R) |  |  | 1365464.1915 | $ /ton NOx(R) |  |  |  | 1399738.9176 | $ /ton NOx(R)
|  |  | 8304-01-07 |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 7 |  | Solar Titan 130 - new oil fired turbine |  |  |  | Solar Titan 130 - new oil fired turbine |  |  |  |  | Solar Titan 130 - new oil fired turbine
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | (Primary fuel No. 2 oil) |  |  |  | (Primary fuel No. 2 oil) |  |  |  |  | (Primary fuel No. 2 oil)
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | η ≈ 54% | 0.254 lb/MMBtu | 1.5 |  | η ≈ 54% | 0.287 lb/MMBtu | 0.8 |  |  | η ≈ 54% | 0.287 lb/MMBtu | 0.8
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 9997874.962 | $ TCC/unit | 943729 |  | 9997874.962 | $ TCC/unit | 943728.6689 |  |  | 11209874.962 | $ TCC/unit | 961925.1685
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 531801.8597 | $ TCC / MW nominal capacity |  |  | 531801.8597 | $ TCC / MW nominal capacity |  |  |  | 596269.9448 | $ TCC / MW nominal capacity
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 841377 | $ /ton NOx(R) |  |  | 1658762.8239 | $ /ton NOx(R) |  |  |  | 1752707.9639 | $ /ton NOx(R)
[16 empty] | Unit NOx Rate - | lb/MMBtu |  |  | Unit NOx Rate - | lb/MMBtu |  |  |  | Unit NOx Rate - | lb/MMBtu
[7 empty] | 2: TURBINES | [9 empty] | Note: | Section III, Turbines' HPWI and SCR - TCC based on EPA1993 ACT re: 2011
PSEG Power LLC, PSEG Fossil LLC, PSEG Power Connecticut
8301-01 | PSEG | BHB4 | 8301-01-01 |  | 12 | PSEG Power LLC, PSEG Fossil LLC, PSEG Power Connecticut | 8301 | Bridgeport Harbor Station | BHB4 | 22 | 60 yrs | None | Jet Fuel A (Kerosene K1); | 1 |  | Selective Catalytic Reduction (SCR) |  |  |  | Selective Catalytic Reduction (SCR) |  |  |  |  | Selective Catalytic Reduction (SCR)
|  | #VALUE! |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | #VALUE! |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | η ≈ 90% |  | NOx(R) = N/A |  | η ≈ 90% | 0.068 lb/MMBtu | 0.7 |  |  | η ≈ 90% | 0.068 lb/MMBtu | 0.7
|  | #VALUE! |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 8895118 | $ TCC/unit |  |  | 8895118 | $ TCC/unit | 839636.2129 |  |  | 2685652 | $ TCC/unit | 230457.1872
|  | #VALUE! |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 404323.5455 | $ TCC / MW nominal capacity |  |  | 404323.5455 | $ TCC / MW nominal capacity |  |  |  | 122075.0909 | $ TCC / MW nominal capacity
|  | #VALUE! |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 118997 | $ /ton NOx(R) |  |  | 1166161.4067 | $ /ton NOx(R) |  |  |  | 483568.0375 | $ /ton NOx(R)
|  | #VALUE! | 8301-01-02 |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2 |  | High Pressure Water Injection (HPWI) |  |  |  | High Pressure Water Injection (HPWI) |  |  |  |  | High Pressure Water Injection (HPWI)
|  | #VALUE! |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | #VALUE! |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | η ≈ 60% |  | NOx(R) = N/A |  | η ≈ 60% | 0.270 lb/MMBtu | 0.5 |  |  | η ≈ 60% | 0.270 lb/MMBtu | 0.5
|  | #VALUE! |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 843728 | $ TCC/unit |  |  | 843728 | $ TCC/unit | 79641.9545 |  |  | 1847813 | $ TCC/unit | 158561.7893
|  | #VALUE! |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 38351.2727 | $ TCC / MW nominal capacity |  |  | 38351.2727 | $ TCC / MW nominal capacity |  |  |  | 83991.5 | $ TCC / MW nominal capacity
|  | #VALUE! |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 839358 | $ /ton NOx(R) |  |  | 165920.7384 | $ /ton NOx(R) |  |  |  | 494552.1132 | $ /ton NOx(R)
[16 empty] | Unit NOx Rate - | lb/MMBtu |  |  | Unit NOx Rate - | lb/MMBtu |  |  |  | Unit NOx Rate - | lb/MMBtu
TURBINES
NRG Energy, Inc
8300-01 | NRG | BR10 | 8300-01-01 |  | 13 | NRG Energy, Inc | 8300 | Branford | BR10 | 20 | 57 yrs | None, per NRG report; Water Injection since Jun 2008 per EPA. | Ultra low sulfur kerosene oil (ULSD); | 1 |  | High Pressure Water Injection (HPWI) |  |  |  | High Pressure Water Injection (HPWI) |  |  |  |  | High Pressure Water Injection (HPWI)
[6 empty] | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | η ≈ 74% | 0.220 lb/MMBtu | 2.5 |  | η ≈ 73% | 0.200 lb/MMBtu | 2.6 |  |  | η ≈ 73% | 0.200 lb/MMBtu | 2.6
[6 empty] | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 2409779 | $ TCC/unit | 299054 |  | 2259168.12 | $ TCC/unit | 213249.4886 |  |  | 1725675 | $ TCC/unit | 148081.0643
[6 empty] | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 120488.95 | $ TCC/MW nom |  |  | 112958.406 | $ TCC / MW nominal capacity |  |  |  | 86283.75 | $ TCC / MW nominal capacity
[6 empty] | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 162782 | $ /ton NOx(R) |  |  | 140368.8053 | $ /ton NOx(R) |  |  |  | 87856.0337 | $ /ton NOx(R)
8300-02 | NRG | CC10 | 8300-02-01 |  | 14 |  |  | Cos Cob | CC10 | 20 | 57 yrs | Water Injection | Ultra low sulfur kerosene oil (ULSD); | No option proposed |  | Control option data not provided - No additional NOx controls are feasible, per NRG. |  |  |  | Control option data not provided - No additional NOx controls are feasible, per NRG. |  |  |  |  | Control option data not provided - No additional NOx controls are feasible, per NRG.
8300-03 | NRG | CC11 |  |  | 15 |  | 4: Cos Cob; 5: CC11; 6: 20; 7: 57 yrs; 8: Water Injection
8300-04 | NRG | CC12 |  |  | 16 |  | 4: Cos Cob; 5: CC12; 6: 20; 7: 57 yrs; 8: Water Injection | These units Stack Test data (FLER= 0.22 lb/MMBtu) is taken as reference for other facilities as Controlled NOx Rate estimate if HPWI technology is applied. |  |  |  | These units Stack Test data (FLER= 0.22 lb/MMBtu) is taken as reference for other facilities as Controlled NOx Rate estimate if HPWI technology is applied. |  |  |  |  | These units Stack Test data (FLER= 0.22 lb/MMBtu) is taken as reference for other facilities as Controlled NOx Rate estimate if HPWI technology is applied.
8300-05 | NRG | CC13 | 8300-05-01 |  | 17 |  |  | Cos Cob | CC13 | 20 | 57 yrs | Water Injection | Ultra low sulfur kerosene oil (ULSD); Natural Gas
8300-06 | NRG | CC14 |  |  | 18 |  | 4: Cos Cob; 5: CC14; 6: 20; 7: 57 yrs; 8: Water Injection
8300-07 | NRG | FD10 | 8300-07-01 |  | 19 |  |  | Franklin Drive | FD10 | 20 | 58 yrs | None | Ultra low sulfur kerosene oil (ULSD); | 1 |  | High Pressure Water Injection (HPWI) |  |  |  | High Pressure Water Injection (HPWI) |  |  |  |  | High Pressure Water Injection (HPWI)
8300-08 | NRG | TT10 | [5 empty] | Torrington Terminal | TT10 | 20 | 58 yrs | None | Ultra low sulfur kerosene oil (ULSD);
8300-09 | NRG | MD10 | [5 empty] | Middletown | MD10 | 20 | 60 yrs | None | Ultra low sulfur kerosene oil (ULSD); |  |  | η ≈ 71% | 0.220 lb/MMBtu | 3 |  | η ≈ 73% | 0.209 lb/MMBtu | 3.2 |  |  | η ≈ 73% | 0.209 lb/MMBtu | 3.2
8300-10 | NRG | NH10 | [5 empty] | Norwalk Harbor Station | NH10 | 17 | 60 yrs | None | No.2 Oil; |  |  | 2409779 | $ TCC/unit | 299054 |  | 2259168.12 | $ TCC/unit | 213249.4886 |  |  | 1725675 | $ TCC/unit | 148081.0643
8300-11 | NRG | DV10 | [5 empty] | Devon | DV10 | 20 | 38 yrs | None | Ultra low sulfur kerosene oil (ULSD); |  |  | 120488.95 | $ TCC / MW nominal capacity |  |  | 112958.406 | $ TCC / MW nominal capacity |  |  |  | 86283.75 | $ TCC / MW nominal capacity
8300-12 | NRG | DV11 | [5 empty] | Devon | DV11 | 40 | 30 yrs | HPWI | ULSD oil; Natural Gas |  |  | 131838 | $ /ton NOx(R) |  |  | 113596.2367 | $ /ton NOx(R) |  |  |  | 71533.0587 | $ /ton NOx(R)
8300-08 | NRG | TT10 | 8300-08-01 |  | 20 |  |  | Torrington Terminal | TT10 | 20 | 58 yrs | None | Ultra low sulfur kerosene oil (ULSD); | 1 |  | High Pressure Water Injection (HPWI) |  |  |  | High Pressure Water Injection (HPWI) |  |  |  |  | High Pressure Water Injection (HPWI)
[6 empty] | #N/A | 4: #N/A; 8: #N/A; 9: #N/A
[6 empty] | #N/A | 4: #N/A; 8: #N/A; 9: #N/A | η ≈ 72% | 0.220 lb/MMBtu | 2.3 |  | η ≈ 73% | 0.187 lb/MMBtu | 2.2 |  |  | η ≈ 73% | 0.187 lb/MMBtu | 2.2
[6 empty] | #N/A | 4: #N/A; 8: #N/A; 9: #N/A | 2409779 | $ TCC/unit | 299054 |  | 2259168.12 | $ TCC/unit | 213249.4886 |  |  | 1725675 | $ TCC/unit | 148081.0643
[6 empty] | #N/A | 4: #N/A; 8: #N/A; 9: #N/A | 120488.95 | $ TCC / MW nominal capacity |  |  | 112958.406 | $ TCC / MW nominal capacity |  |  |  | 86283.75 | $ TCC / MW nominal capacity
[6 empty] | #N/A | 4: #N/A; 8: #N/A; 9: #N/A | 172961 | $ /ton NOx(R) |  |  | 161104.9571 | $ /ton NOx(R) |  |  |  | 100547.097 | $ /ton NOx(R)
[16 empty] | Unit NOx Rate - | lb/MMBtu |  |  | Unit NOx Rate - | lb/MMBtu |  |  |  | Unit NOx Rate - | lb/MMBtu
[7 empty] | 2: TURBINES | [9 empty] | Note: | Section III, Turbines' HPWI and SCR - TCC based on EPA1993 ACT re: 2011
NRG Energy, Inc
8300-09 | NRG | MD10 | 8300-09-01 |  | 21 |  | 8300 | Middletown | MD10 | 20 | 60 yrs | None | Ultra low sulfur kerosene oil (ULSD); | 1 |  | High Pressure Water Injection (HPWI) |  |  |  | High Pressure Water Injection (HPWI) |  |  |  |  | High Pressure Water Injection (HPWI)
[6 empty] | #N/A | 4: #N/A; 8: #N/A; 9: #N/A
[6 empty] | #N/A | 4: #N/A; 8: #N/A; 9: #N/A | η ≈ 68% | 0.220 lb/MMBtu | 4.2 |  | η ≈ 67% | 0.187 lb/MMBtu | 4.5 |  |  | η ≈ 67% | 0.187 lb/MMBtu | 4.5
[6 empty] | #N/A | 4: #N/A; 8: #N/A; 9: #N/A | 2304179 | $ TCC/unit | 285949 |  | 2160168.12 | $ TCC/unit | 203904.5889 |  |  | 1725675 | $ TCC/unit | 148081.0643
[6 empty] | #N/A | 4: #N/A; 8: #N/A; 9: #N/A | 115208.95 | $ TCC / MW nominal capacity |  |  | 108008.406 | $ TCC / MW nominal capacity |  |  |  | 86283.75 | $ TCC / MW nominal capacity
[6 empty] | #N/A | 4: #N/A; 8: #N/A; 9: #N/A | 92830 | $ /ton NOx(R) |  |  | 76390.3249 | $ /ton NOx(R) |  |  |  | 52217.7369 | $ /ton NOx(R)
8300-10 | NRG | NH10 | 8300-10-01 |  | 22 |  |  | Norwalk Harbor Station | NH10 | 17 | 60 yrs | None | No.2 Oil; | 1 |  | High Pressure Water Injection (HPWI) |  |  |  | High Pressure Water Injection (HPWI) |  |  |  |  | High Pressure Water Injection (HPWI)
[6 empty] | #N/A | 4: #N/A; 8: #N/A; 9: #N/A
[6 empty] | #N/A | 4: #N/A; 8: #N/A; 9: #N/A | η ≈ 50% | 0.260 lb/MMBtu | 0.5 |  | η ≈ 50% | 0.257 lb/MMBtu | 0.6 |  |  | η ≈ 50% | 0.257 lb/MMBtu | 0.6
[6 empty] | #N/A | 4: #N/A; 8: #N/A; 9: #N/A | 1592321 | $ TCC/unit | 409374 |  | 1468823.4 | $ TCC/unit | 138646.5381 |  |  | 1542468 | $ TCC/unit | 132359.9769
[6 empty] | #N/A | 4: #N/A; 8: #N/A; 9: #N/A | 93665.9412 | $ TCC / MW nominal capacity |  |  | 86401.3765 | $ TCC / MW nominal capacity |  |  |  | 90733.4118 | $ TCC / MW nominal capacity
[6 empty] | #N/A | 4: #N/A; 8: #N/A; 9: #N/A | 990785 | $ /ton NOx(R) |  |  | 406515.8194 | $ /ton NOx(R) |  |  |  | 318608.6452 | $ /ton NOx(R)
8300-11 | NRG | DV10 | 8300-11-01 |  | 23 | NRG Energy, Inc |  | Devon | DV10 | 20 | 38 yrs | None | Ultra low sulfur kerosene oil (ULSD); | 1 |  | Selective Catalytic Reduction (SCR) |  |  |  | Selective Catalytic Reduction (SCR) |  |  |  |  | Selective Catalytic Reduction (SCR)
|  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | η ≈ 87% | 0.100 lb/MMBtu | 1.6 |  | η ≈ 90% | 0.067 lb/MMBtu | 1.7 |  |  | η ≈ 90% | 0.067 lb/MMBtu | 1.7
|  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 6494100 | $ TCC/unit | 805651 |  | 6076337.9292 | $ TCC/unit | 573563.3149 |  |  | 2513690 | $ TCC/unit | 215701.039
|  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 324705 | $ TCC / MW nominal capacity |  |  | 303816.8965 | $ TCC / MW nominal capacity |  |  |  | 125684.5 | $ TCC / MW nominal capacity
|  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 602932 | $ /ton NOx(R) |  |  | 491765.8834 | $ /ton NOx(R) |  |  |  | 194624.0926 | $ /ton NOx(R)
|  | #N/A | 8300-11-02 |  |  | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2 |  | High Pressure Water Injection (HPWI) |  |  |  | High Pressure Water Injection (HPWI) |  |  |  |  | High Pressure Water Injection (HPWI)
|  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | η ≈ 72% | 0.220 lb/MMBtu | 1.3 |  | η ≈ 70% | 0.199 lb/MMBtu | 1.3 |  |  | η ≈ 70% | 0.199 lb/MMBtu | 1.3
|  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 1800467 | $ TCC/unit | 223438 |  | 1687938.12 | $ TCC/unit | 159329.4176 |  |  | 1725675 | $ TCC/unit | 148081.0643
|  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 90023.35 | $ TCC / MW nominal capacity |  |  | 84396.906 | $ TCC / MW nominal capacity |  |  |  | 86283.75 | $ TCC / MW nominal capacity
|  | #N/A |  |  |  | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 247900 | $ /ton NOx(R) |  |  | 215538.4383 | $ /ton NOx(R) |  |  |  | 169313.9851 | $ /ton NOx(R)
8300-12 | NRG | DV11 | 8300-12-01 |  | 24 |  |  | Devon | DV11 | 40 | 30 yrs | HPWI | ULSD oil; Natural Gas | 1 |  | Selective Catalytic Reduction (SCR) |  |  |  | Selective Catalytic Reduction (SCR) |  |  |  |  | Selective Catalytic Reduction (SCR)
|  | #N/A |  |  |  | #N/A | 4: #N/A; 5: #N/A; 6: #N/A; 7: #N/A; 8: #N/A
|  | #N/A |  |  |  | #N/A | 4: #N/A; 5: #N/A; 6: #N/A; 7: #N/A; 8: #N/A
8300-13 | NRG | DV12 |  |  | 25 |  |  | Devon | DV12 | 40 | 30 yrs | HPWI | ULSD oil; Natural Gas |  |  | η ≈ 71% | 0.050 lb/MMBtu | 1.9 |  | η ≈ 90% | 0.015 lb/MMBtu | 2.1 |  |  | η ≈ 90% | 0.015 lb/MMBtu | 2.1
|  | #N/A |  |  |  | #N/A | 4: #N/A; 5: #N/A; 6: #N/A; 7: #N/A; 8: #N/A
|  | #N/A |  |  |  | #N/A | 4: #N/A; 5: #N/A; 6: #N/A; 7: #N/A; 8: #N/A | 11462246.5 | $ TCC/unit | 673515.5 |  | 10741401 | $ TCC/unit | 1013912.267 |  |  | 4233310 | $ TCC/unit | 363262.5207
8300-14 | NRG | DV13 |  |  | 26 |  |  | Devon | DV13 | 40 | 30 yrs | HPWI | ULSD oil; Natural Gas | [13 empty] | 0
|  | #N/A |  |  |  | #N/A | 4: #N/A; 5: #N/A; 6: #N/A; 7: #N/A; 8: #N/A | 286556.1625 | $ TCC / MW nominal capacity |  |  | 268535.025 | $ TCC / MW nominal capacity |  |  |  | 105832.75 | $ TCC / MW nominal capacity
|  | #N/A |  |  |  | #N/A | 4: #N/A; 5: #N/A; 6: #N/A; 7: #N/A; 8: #N/A
8300-15 | NRG | DV14 |  |  | 27 |  |  | Devon | DV14 | 40 | 30 yrs | HPWI | ULSD oil; Natural Gas |  |  | 477897 | $ /ton NOx(R) |  |  | 544839.7473 | $ /ton NOx(R) |  |  |  | 275837.4098 | $ /ton NOx(R)
|  | #N/A |  |  |  | #N/A | 4: #N/A; 5: #N/A; 6: #N/A; 7: #N/A; 8: #N/A
|  | #N/A |  |  |  | #N/A | 4: #N/A; 5: #N/A; 6: #N/A; 7: #N/A; 8: #N/A
[16 empty] | Unit NOx Rate - | lb/MMBtu |  |  | Unit NOx Rate - | lb/MMBtu |  |  |  | Unit NOx Rate - | lb/MMBtu
[7 empty] | 2: DIESEL ENGINES | Note: | [8 empty] | Note: | Section III, Diesel Engine SCR - TCC based on EPA1993 ACT re: 2011
[7 empty] | 2: NRG Energy, Inc | SCR Efficiency, η = 70% - per NRG
8300-16 | NRG | MV10 | 8300-16-01 |  | 1 | NRG Energy, Inc | 8300 | Montville | MV10 | 2.75 | 61 yrs | None | 0.05% sulfur distillate oil; | 1 |  | Selective Catalytic Reduction (SCR) |  |  |  | Selective Catalytic Reduction (SCR) |  |  |  |  | Selective Catalytic Reduction (SCR)
|  | 0 |  |  |  |  | 8: #N/A; 9: #N/A
|  | 0 |  |  |  |  | 8: #N/A; 9: #N/A | η ≈ 70% | 0.933 lb/MMBtu | 4.2 |  | η ≈ 90% | 0.311 lb/MMBtu | 12.8 |  |  | η ≈ 90% | 0.311 lb/MMBtu | 12.8
8300-17 | NRG | MV11 |  |  |  |  | 5: MV11; 6: 2.75; 7: 61 yrs; 8: None; 9: #VALUE! | 1129075 | $ TCC/unit | 290277 |  | 1058508 | $ TCC/unit | 99915.667 |  |  | 1030517.75 | $ TCC/unit | 88429.2611
|  | 0 |  |  |  |  | 8: #N/A; 9: #N/A | 410572.7273 | $ TCC / MW nominal capacity |  |  | 384912 | $ TCC / MW nominal capacity |  |  |  | 374733.7273 | $ TCC / MW nominal capacity
|  | 0 |  |  |  |  | 8: #N/A; 9: #N/A | 79606 | $ /ton NOx(R) |  |  | 11200.4337 | $ /ton NOx(R) |  |  |  | 16751.9333 | $ /ton NOx(R)
[16 empty] | Unit NOx Rate - | lb/MMBtu |  |  | Unit NOx Rate - | lb/MMBtu |  |  |  | Unit NOx Rate - | lb/MMBtu
[21 empty] | UTILITY BOILERS - CRF |  |  |  |  | UTILITY BOILERS - CRF
[21 empty] | n | 40 |  |  |  | n | 40
[21 empty] | i% | 7% |  |  |  | i% | 7%
[7 empty] | 2: UTILITY BOLIERS | [5 empty] | CRF | 0.075009 |  |  |  | CRF | 0.075009
NRG Energy, Inc
8306-01 | NRG | MD2 | 8306-01-01 |  | 1 | NRG Energy, Inc | 8306 | Middletown | MD2 | 120 |  | None | No. 6 oil; No. 2 oil | 1 |  | Rotating Opposed Fire Air (ROFA) |  |  |  | Rotating Opposed Fire Air (ROFA) |  |  |  |  | Rotating Opposed Fire Air (ROFA)
|  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A
|  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  |  | η ≈ 17% | 0.150 lb/MMBtu | 15.3 |  | η ≈ 35% | 0.085 lb/MMBtu | 33 |  |  | η ≈ 35% | 0.085 lb/MMBtu | 33
|  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  |  | 6191538.8944 | $ TCC/unit | 1591798 |  | 6191538.8455 | $ TCC/unit | 464421.9971 |  |  | 6191538.8455 | $ TCC/unit | 464421.9971
|  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  |  | 51596.1575 | $ TCC / MW nominal capacity |  |  | 51596.157 | $ TCC / MW nominal capacity |  |  |  | 51596.157 | $ TCC / MW nominal capacity
|  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  |  | 115582 | $ /ton NOx(R) |  |  | 19323.9004 | $ /ton NOx(R) |  |  |  | 57787.4016 | $ /ton NOx(R)
|  | #N/A | 8306-01-02 |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | 2 |  | Selective Catalytic Reduction (SCR) with ID fans |  |  |  | Selective Catalytic Reduction (SCR) with ID fans |  |  |  |  | Selective Catalytic Reduction (SCR) with ID fans
|  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A
|  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  |  | η ≈ 44% | 0.100 lb/MMBtu | 40.7 |  | η ≈ 90% | 0.013 lb/MMBtu | 84.8 |  |  | η ≈ 90% | 0.013 lb/MMBtu | 84.8
|  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  |  | 65903462 | $ TCC/unit | 16943283 |  | 65903462 | $ TCC/unit | 4943361.9334 |  |  | 11111790 | $ TCC/unit | 833485.7992
|  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  |  | 549195.5167 | $ TCC / MW nominal capacity |  |  | 549195.5167 | $ TCC / MW nominal capacity |  |  |  | 92598.25 | $ TCC / MW nominal capacity
|  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  |  | 420384 | $ /ton NOx(R) |  |  | 60317.9398 | $ /ton NOx(R) |  |  |  | 30364.835 | $ /ton NOx(R)
8306-02 | NRG | MD3 | 8306-02-01 |  | 2 |  | 8306 | Middletown | MD3 | 236 |  | None | No. 6 oil; No. 2 oil | 1 |  | Separated Overfired Air / High Energy Reagent Technology (SOFA/HERT) |  |  |  | Separated Overfired Air / High Energy Reagent Technology (SOFA/HERT) |  |  |  |  | Separated Overfired Air / High Energy Reagent Technology (SOFA/HERT)
|  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | η ≈ 44% | 0.150 lb/MMBtu | 74 |  | η ≈ 44% | 0.117 lb/MMBtu | 84.1 |  |  | η ≈ 44% | 0.117 lb/MMBtu | 84.1
|  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 4644454.5454 | $ TCC/unit | 1194055 |  | 4639455.6319 | $ TCC/unit | 348001.5718 |  |  | 4639455.6319 | $ TCC/unit | 348001.5718
|  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 19679.8921 | $ TCC / MW nominal capacity |  |  | 19658.7103 | $ TCC / MW nominal capacity |  |  |  | 19658.7103 | $ TCC / MW nominal capacity
|  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 20803 | $ /ton NOx(R) |  |  | 8240.7358 | $ /ton NOx(R) |  |  |  | 22891.6355 | $ /ton NOx(R)
|  | #N/A | 8306-02-02 |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2 |  | Selective Catalytic Reduction (SCR) with ID fans |  |  |  | Selective Catalytic Reduction (SCR) with ID fans |  |  |  |  | Selective Catalytic Reduction (SCR) with ID fans
|  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | η ≈ 63% | 0.100 lb/MMBtu | 104.8 |  | η ≈ 90% | 0.021 lb/MMBtu | 170.4 |  |  | η ≈ 90% | 0.021 lb/MMBtu | 170.4
|  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 101740653.5 | $ TCC/unit | 26156755 |  | 101740653.5 | $ TCC/unit | 7631478.8075 |  |  | 101740653.5 | $ TCC/unit | 7631478.8075
|  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 431104.464 | $ TCC / MW nominal capacity |  |  | 431104.464 | $ TCC / MW nominal capacity |  |  |  | 431104.464 | $ TCC / MW nominal capacity
|  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 251477 | $ /ton NOx(R) |  |  | 45997.0876 | $ /ton NOx(R) |  |  |  | 59071.2095 | $ /ton NOx(R)
8306-03 | NRG | MD4 | 8306-03-01 |  | 3 |  | 8306 | Middletown | MD4 | 400 |  | None | No. 6 oil; No. 2 oil | 1 |  | Separated Overfired Air / High Energy Reagent Technology (SOFA/HERT) |  |  |  | Separated Overfired Air / High Energy Reagent Technology (SOFA/HERT) |  |  |  |  | Separated Overfired Air / High Energy Reagent Technology (SOFA/HERT)
|  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | η ≈ 46% | 0.150 lb/MMBtu | 36.3 |  | η ≈ 46% | 0.098 lb/MMBtu | 37.4 |  |  | η ≈ 46% | 0.098 lb/MMBtu | 37.4
|  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 6213828.4982 | $ TCC/unit | 1597528 |  | 6083835.4149 | $ TCC/unit | 456343.2555 |  |  | 6083835.4149 | $ TCC/unit | 456343.2555
|  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 15534.5712 | $ TCC / MW nominal capacity |  |  | 15209.5885 | $ TCC / MW nominal capacity |  |  |  | 15209.5885 | $ TCC / MW nominal capacity
|  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 49103 | $ /ton NOx(R) |  |  | 17098.5754 | $ /ton NOx(R) |  |  |  | 34830.1394 | $ /ton NOx(R)
|  | 0 | 8306-03-02 |  |  |  | 8: #N/A; 10: 2 | Selective Catalytic Reduction (SCR) with ID fans |  |  |  | Selective Catalytic Reduction (SCR) with ID fans |  |  |  |  | Selective Catalytic Reduction (SCR) with ID fans
|  | 0 |  |  |  |  | 8: #N/A
|  | 0 |  |  |  |  | 8: #N/A | η ≈ 64% | 0.100 lb/MMBtu | 50.2 |  | η ≈ 90% | 0.018 lb/MMBtu | 72.5 |  |  | η ≈ 90% | 0.018 lb/MMBtu | 72.5
|  | 0 |  |  |  |  | 8: #N/A | 145353268 | $ TCC/unit | 37369229 |  | 145353268 | $ TCC/unit | 10902823.4651 |  |  | 145353268 | $ TCC/unit | 10902823.4651
|  | 0 |  |  |  |  | 8: #N/A
|  | 0 |  |  |  |  | 8: #N/A | 746981 | $ /ton NOx(R) |  |  | 152263.954 | $ /ton NOx(R) |  |  |  | 244868.8301 | $ /ton NOx(R)
|  | #N/A | 8306-03-03 |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3 |  | Selective Catalytic Reduction (SCR) |  |  |  | Selective Catalytic Reduction (SCR) |  |  |  |  | Selective Catalytic Reduction (SCR)
|  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | η ≈ 64% | 0.100 lb/MMBtu | 50.2 |  | η ≈ 90% | 0.018 lb/MMBtu | 72.5 |  |  | η ≈ 90% | 0.018 lb/MMBtu | 72.5
|  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 106812093 | $ TCC/unit | 27460583 |  | 106812093 | $ TCC/unit | 8011883.1172 |  |  | 106812093 | $ TCC/unit | 9165600.9458
|  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 267030.2325 | $ TCC / MW nominal capacity |  |  | 267030.2325 | $ TCC / MW nominal capacity |  |  |  | 267030.2325 | $ TCC / MW nominal capacity
|  | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 548385 | $ /ton NOx(R) |  |  | 111522.7897 | $ /ton NOx(R) |  |  |  | 139936.6889 | $ /ton NOx(R)
[16 empty] | Unit NOx Rate - | lb/MMBtu |  |  | Unit NOx Rate - | lb/MMBtu |  |  |  | Unit NOx Rate - | lb/MMBtu
[23 empty] | Note: | Since MD2 is an 120MW boiler (< 160MW), Section III, MD2 SCR Total Capital Cost assessd per EPA1993 ACT re: 2011
UTILITY BOLIERS
NRG Energy, Inc
8306-04 | NRG | MV5 | 8306-04-01 |  | 4 | NRG Energy, Inc | 8306 | Montville | MV5 | 81 |  | None | No. 6 oil; Nat. Gas | 1 |  | Close Coupled Over Fire Air (CCOFA) |  |  |  | Close Coupled Over Fire Air (CCOFA) |  |  |  |  | Close Coupled Over Fire Air (CCOFA)
|  | #N/A |  |  |  |  | 5: #N/A; 6: #N/A; 7: #N/A; 8: #N/A; 9: #N/A
|  | #N/A |  |  |  |  | 5: #N/A; 6: #N/A; 7: #N/A; 8: #N/A; 9: #N/A | η ≈ 35% | 0.150 lb/MMBtu | 14.1 |  | η ≈ 35% | 0.063 lb/MMBtu | 9.5 |  |  | η ≈ 35% | 0.063 lb/MMBtu | 9.5
|  | #N/A |  |  |  |  | 5: #N/A; 6: #N/A; 7: #N/A; 8: #N/A; 9: #N/A | 1950049.784 | $ TCC/unit | 501343 |  | 1950049.784 | $ TCC/unit | 146271.5551 |  |  | 1950049.784 | $ TCC/unit | 146271.5551
|  | #N/A |  |  |  |  | 5: #N/A; 6: #N/A; 7: #N/A; 8: #N/A; 9: #N/A | 24074.6887 | $ TCC / MW nominal capacity |  |  | 24074.6887 | $ TCC / MW nominal capacity |  |  |  | 24074.6887 | $ TCC / MW nominal capacity
|  | #N/A |  |  |  |  | 5: #N/A; 6: #N/A; 7: #N/A; 8: #N/A; 9: #N/A | 37271 | $ /ton NOx(R) |  |  | 17920.332 | $ /ton NOx(R) |  |  |  | 80160.0378 | $ /ton NOx(R)
|  | #N/A | 8306-04-02 | [5 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | 2 |  | (HERT) High Energy Reagent Technology SNCR |  |  |  | (HERT) High Energy Reagent Technology SNCR |  |  |  |  | (HERT) High Energy Reagent Technology SNCR
|  | #N/A |  |  |  |  | 5: #N/A; 6: #N/A; 7: #N/A; 8: #N/A; 9: #N/A
|  | #N/A |  |  |  |  | 5: #N/A; 6: #N/A; 7: #N/A; 8: #N/A; 9: #N/A | η ≈ 35% | 0.150 lb/MMBtu | 14.1 |  | η ≈ 35% | 0.063 lb/MMBtu | 9.5 |  |  | η ≈ 35% | 0.063 lb/MMBtu | 9.5
|  | #N/A |  |  |  |  | 5: #N/A; 6: #N/A; 7: #N/A; 8: #N/A; 9: #N/A | 1602412.9684 | $ TCC/unit | 411968 |  | 1602412.9684 | $ TCC/unit | 120195.6169 |  |  | 1602412.9684 | $ TCC/unit | 120195.6169
|  | #N/A |  |  |  |  | 5: #N/A; 6: #N/A; 7: #N/A; 8: #N/A; 9: #N/A | 19782.8762 | $ TCC / MW nominal capacity |  |  | 19782.8762 | $ TCC / MW nominal capacity |  |  |  | 19782.8762 | $ TCC / MW nominal capacity
|  | #N/A |  |  |  |  | 5: #N/A; 6: #N/A; 7: #N/A; 8: #N/A; 9: #N/A | 40372 | $ /ton NOx(R) |  |  | 29154.0337 | $ /ton NOx(R) |  |  |  | 75760.9315 | $ /ton NOx(R)
|  | #N/A | 8306-04-03 | [5 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | 3 |  | Selective Catalytic Reduction (SCR) |  |  |  | Selective Catalytic Reduction (SCR) |  |  |  |  | Selective Catalytic Reduction (SCR)
|  | #N/A |  |  |  |  | 5: #N/A; 6: #N/A; 7: #N/A; 8: #N/A; 9: #N/A
|  | #N/A |  |  |  |  | 5: #N/A; 6: #N/A; 7: #N/A; 8: #N/A; 9: #N/A | η ≈ 35% | 0.150 lb/MMBtu | 14.1 |  | η ≈ 90% | 0.010 lb/MMBtu | 24.7 |  |  | η ≈ 90% | 0.010 lb/MMBtu | 24.7
|  | #N/A |  |  |  |  | 5: #N/A; 6: #N/A; 7: #N/A; 8: #N/A; 9: #N/A | 65452696 | $ TCC/unit | 16827394 |  | 65452696 | $ TCC/unit | 4909550.3639 |  |  | 7758531 | $ TCC/unit | 581960.7292
|  | #N/A |  |  |  |  | 5: #N/A; 6: #N/A; 7: #N/A; 8: #N/A; 9: #N/A | 808057.9753 | $ TCC / MW nominal capacity |  |  | 808057.9753 | $ TCC / MW nominal capacity |  |  |  | 95784.3333 | $ TCC / MW nominal capacity
|  | #N/A |  |  |  |  | 5: #N/A; 6: #N/A; 7: #N/A; 8: #N/A; 9: #N/A | 1196986 | $ /ton NOx(R) |  |  | 201568.2224 | $ /ton NOx(R) |  |  |  | 60024.773 | $ /ton NOx(R)
8306-05 | NRG | MV6 | 8306-05-01 |  | 5 |  | 5: MV6; 6: 402; 8: None; 9: No. 6 oil; No. 2 oil; 10: 1 | Separated Overfired Air / High Energy Reagent Technology (SOFA/HERT) |  |  |  | Separated Overfired Air / High Energy Reagent Technology (SOFA/HERT) |  |  |  |  | Separated Overfired Air / High Energy Reagent Technology (SOFA/HERT)
|  | 0 |  |  |  |  | 8: #N/A
|  | 0 |  |  |  |  | 8: #N/A | η ≈ 44% | 0.150 lb/MMBtu | 26.9 |  | η ≈ 44% | 0.081 lb/MMBtu | 19.7 |  |  | η ≈ 44% | 0.081 lb/MMBtu | 19.7
|  | 0 |  |  |  |  | 8: #N/A | 6077988.9799 | $ TCC/unit | 1562605 |  | 6058988.9799 | $ TCC/unit | 454479.5458 |  |  | 6058988.9799 | $ TCC/unit | 454479.5458
|  | 0 |  |  |  |  | 8: #N/A | 15119.3756 | $ TCC / MW nominal capacity |  |  | 15072.1119 | $ TCC / MW nominal capacity |  |  |  | 15072.1119 | $ TCC / MW nominal capacity
|  | 0 |  |  |  |  | 8: #N/A | 64961 | $ /ton NOx(R) |  |  | 32412.776 | $ /ton NOx(R) |  |  |  | 60331.5557 | $ /ton NOx(R)
|  | 0 | 8306-05-02 |  |  |  | 8: #N/A; 10: 2 | Selective Catalytic Reduction (SCR) with ID fans |  |  |  | Selective Catalytic Reduction (SCR) with ID fans |  |  |  |  | Selective Catalytic Reduction (SCR) with ID fans
|  | 0 |  |  |  |  | 8: #N/A
|  | 0 |  |  |  |  | 8: #N/A | η ≈ 63% | 0.100 lb/MMBtu | 38.1 |  | η ≈ 90% | 0.015 lb/MMBtu | 39.9 |  |  | η ≈ 90% | 0.015 lb/MMBtu | 39.9
|  | 0 |  |  |  |  | 8: #N/A | 145353268 | $ TCC/unit | 37369229 |  | 145353268 | $ TCC/unit | 10902823.4651 |  |  | 145353268 | $ TCC/unit | 10902823.4651
|  | 0 |  |  |  |  | 8: #N/A | 361575.2935 | $ TCC / MW nominal capacity |  |  | 361575.2935 | $ TCC / MW nominal capacity |  |  |  | 361575.2935 | $ TCC / MW nominal capacity
|  | 0 |  |  |  |  | 8: #N/A | 984549 | $ /ton NOx(R) |  |  | 276602.6954 | $ /ton NOx(R) |  |  |  | 440010.5732 | $ /ton NOx(R)
|  | 0 | 8306-05-03 |  |  |  | 8: #N/A; 10: 3 | Selective Catalytic Reduction (SCR) |  |  |  | Selective Catalytic Reduction (SCR) |  |  |  |  | Selective Catalytic Reduction (SCR)
|  | 0 |  |  |  |  | 8: #N/A
|  | 0 |  |  |  |  | 8: #N/A | η ≈ 63% | 0.100 lb/MMBtu | 38.1 |  | η ≈ 90% | 0.015 lb/MMBtu | 39.9 |  |  | η ≈ 90% | 0.015 lb/MMBtu | 39.9
|  | 0 |  |  |  |  | 8: #N/A | 106812093 | $ TCC/unit | 27460583 |  | 106812093 | $ TCC/unit | 8011883.1172 |  |  | 106812093 | $ TCC/unit | 8011883.1172
|  | 0 |  |  |  |  | 8: #N/A | 265701.7239 | $ TCC / MW nominal capacity |  |  | 265701.7239 | $ TCC / MW nominal capacity |  |  |  | 265701.7239 | $ TCC / MW nominal capacity
|  | 0 |  |  |  |  | 8: #N/A | 722811 | $ /ton NOx(R) |  |  | 202610.5121 | $ /ton NOx(R) |  |  |  | 250923.9883 | $ /ton NOx(R)
[16 empty] | Unit NOx Rate - | lb/MMBtu |  |  | Unit NOx Rate - | lb/MMBtu |  |  |  | Unit NOx Rate - | lb/MMBtu
[24 empty] | Note: | Since MV5 is an 81 MW bolier (< 160MW), Section III, MV5 SCR Total Capital Cost assessed per EPA1993 ACT re: 2011
UTILITY BOLIERS
NRG Energy, Inc
8306-06 | NRG | NH1 | 8306-06-01 |  | 6 | NRG Energy, Inc | 8306 | Norwalk Harbor Station | NH1 | 164 |  | None | No. 6 oil; No. 2 oil | 1 |  | Separated Overfired Air / High Energy Reagent Technology (SOFA/HERT) |  |  |  | Separated Overfired Air / High Energy Reagent Technology (SOFA/HERT) |  |  |  |  | Separated Overfired Air / High Energy Reagent Technology (SOFA/HERT)
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | η ≈ 29% | 0.150 lb/MMBtu | 9 |  | η ≈ 29% | 0.113 lb/MMBtu | 14.1 |  |  | η ≈ 29% | 0.113 lb/MMBtu | 14.1
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 5857062.783 | $ TCC/unit | 1505807 |  | 5852064.0305 | $ TCC/unit | 438958.2836 |  |  | 5852064.0305 | $ TCC/unit | 438958.2836
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 35713.7975 | $ TCC / MW nominal capacity |  |  | 35683.3173 | $ TCC / MW nominal capacity |  |  |  | 35683.3173 | $ TCC / MW nominal capacity
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 168593 | $ /ton NOx(R) |  |  | 31768.7776 | $ /ton NOx(R) |  |  |  | 105767.6898 | $ /ton NOx(R)
|  |  | 8306-06-02 |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2 |  | Selective Catalytic Reduction (SCR) with ID fans |  |  |  | Selective Catalytic Reduction (SCR) with ID fans |  |  |  |  | Selective Catalytic Reduction (SCR) with ID fans
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | η ≈ 52% | 0.100 lb/MMBtu | 16.5 |  | η ≈ 90% | 0.016 lb/MMBtu | 44.6 |  |  | η ≈ 90% | 0.016 lb/MMBtu | 44.6
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 82710410 | $ TCC/unit | 21264222 |  | 82710410 | $ TCC/unit | 6204036.63 |  |  | 82710410 | $ TCC/unit | 6204036.63
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 504331.7683 | $ TCC / MW nominal capacity |  |  | 504331.7683 | $ TCC / MW nominal capacity |  |  |  | 504331.7683 | $ TCC / MW nominal capacity
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 1294738 | $ /ton NOx(R) |  |  | 141105.738 | $ /ton NOx(R) |  |  |  | 172823.0637 | $ /ton NOx(R)
8306-07 | NRG | NH2 | 8306-07-01 |  | 7 |  | 8306 | Norwalk Harbor Station | NH2 | 172 |  | None | No. 6 oil; No. 2 oil | 1 |  | Separated Overfired Air / High Energy Reagent Technology (SOFA/HERT) |  |  |  | Separated Overfired Air / High Energy Reagent Technology (SOFA/HERT) |  |  |  |  | Separated Overfired Air / High Energy Reagent Technology (SOFA/HERT)
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | η ≈ 29% | 0.150 lb/MMBtu | 11.1 |  | η ≈ 45% | 0.082 lb/MMBtu | 34.5 |  |  | η ≈ 45% | 0.082 lb/MMBtu | 34.5
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 5857062.783 | $ TCC/unit | 1505807 |  | 5852064.0305 | $ TCC/unit | 438958.2836 |  |  | 5852064.0305 | $ TCC/unit | 438958.2836
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 34052.6906 | $ TCC / MW nominal capacity |  |  | 34023.6281 | $ TCC / MW nominal capacity |  |  |  | 34023.6281 | $ TCC / MW nominal capacity
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 136570 | $ /ton NOx(R) |  |  | 13025.9679 | $ /ton NOx(R) |  |  |  | 60087.8111 | $ /ton NOx(R)
|  |  | 8306-07-02 |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2 |  | Selective Catalytic Reduction (SCR) with ID fans |  |  |  | Selective Catalytic Reduction (SCR) with ID fans |  |  |  |  | Selective Catalytic Reduction (SCR) with ID fans
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | η ≈ 52% | 0.100 lb/MMBtu | 20.4 |  | η ≈ 90% | 0.015 lb/MMBtu | 69 |  |  | η ≈ 90% | 0.015 lb/MMBtu | 69
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 82710410 | $ TCC/unit | 21264222 |  | 82710410 | $ TCC/unit | 6204036.63 |  |  | 82710410 | $ TCC/unit | 6204036.63
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 480874.4767 | $ TCC / MW nominal capacity |  |  | 480874.4767 | $ TCC / MW nominal capacity |  |  |  | 480874.4767 | $ TCC / MW nominal capacity
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 1049528 | $ /ton NOx(R) |  |  | 91336.0949 | $ /ton NOx(R) |  |  |  | 121006.3598 | $ /ton NOx(R)
[16 empty] | Unit NOx Rate - | lb/MMBtu |  |  | Unit NOx Rate - | lb/MMBtu |  |  |  | Unit NOx Rate - | lb/MMBtu
UTILITY BOLIERS
PSEG Power LLC, PSEG Fossil LLC, PSEG Power Connecticut
8305-01 | PSEG | NHB1 | 8305-01-01 |  | 8 | PSEG Power LLC, PSEG Fossil LLC, PSEG Power Connecticut | 8305 | New Haven Harbor | NHB1 | Unit is a steam boiler, only | 52 yrs | None | No. 6 oil; | 1 |  | Low NOx Burners (LNB) | #N/A |  |  | Low NOx Burners (LNB) |  |  |  |  | Low NOx Burners (LNB)
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | η ≈ 30% |  | NOx(R) = N/A |  | η ≈ 30% | 0.096 lb/MMBtu | 30.6 |  |  | η ≈ 30% | 0.096 lb/MMBtu | 30.6
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 133450 | $ TCC/unit |  |  | 133450 | $ TCC/unit | 10009.9696 |  |  | 133450 | $ TCC/unit | 10009.9696
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | N/A | $ TCC / MW nominal capacity |  |  | N/A | $ TCC / MW nominal capacity |  |  |  | N/A | $ TCC / MW nominal capacity
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 4448 | $ /ton NOx(R) |  |  | 327.1232 | $ /ton NOx(R) | (see note below) |  |  | 7398.8953 | $ /ton NOx(R)
|  |  | 8305-01-02 |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2 |  | Flue Gas Recirculation (FGR) | #N/A |  |  | Flue Gas Recirculation (FGR) |  |  |  |  | Flue Gas Recirculation (FGR)
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | η ≈ 30% |  | 3.5 |  | η ≈ 30% | 0.096 lb/MMBtu | 30.6 |  |  | η ≈ 30% | 0.096 lb/MMBtu | 30.6
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 101676 | $ TCC/unit |  |  | 101676 | $ TCC/unit | 7626.6292 |  |  | 101676 | $ TCC/unit | 7626.6292
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | N/A | $ TCC / MW nominal capacity |  |  | N/A | $ TCC / MW nominal capacity |  |  |  | N/A | $ TCC / MW nominal capacity
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  | 2797 | $ /ton NOx(R) |  |  | 249.2362 | $ /ton NOx(R) | (see note below) |  |  | 7274.1843 | $ /ton NOx(R)
8305-02 | PSEG | BHB2 | 8305-02-01 |  | 9 |  | 8305 | Bridgeport Harbor Station | BHB2 | 170 | 66 yrs | None | No. 6 oil; No. 2 oil | 1 |  | Selective Catalytic Reduction (SCR) | #N/A |  |  | Selective Catalytic Reduction (SCR) |  |  |  |  | Selective Catalytic Reduction (SCR)
[6 empty] | #N/A | 2: #N/A; 4: #N/A; 8: #N/A
[6 empty] | #N/A | 2: #N/A; 4: #N/A; 8: #N/A | η ≈ 90% |  | 2.1 |  | η ≈ 90% | 0.028 lb/MMBtu | 10.6 |  |  | η ≈ 90% | 0.028 lb/MMBtu | 10.6
[6 empty] | #N/A | 2: #N/A; 4: #N/A; 8: #N/A | 17483068 | $ TCC/unit |  |  | 17483068 | $ TCC/unit | 1311389.8755 |  |  | 17483068 | $ TCC/unit | 1311389.8755
[6 empty] | #N/A | 2: #N/A; 4: #N/A; 8: #N/A | 102841.5765 | $ TCC / MW nominal capacity |  |  | 102841.5765 | $ TCC / MW nominal capacity |  |  |  | 102841.5765 | $ TCC / MW nominal capacity
[6 empty] | #N/A | 2: #N/A; 4: #N/A; 8: #N/A | 290373 | $ /ton NOx(R) |  |  | 123483.0391 | $ /ton NOx(R) | (see note below) |  |  | 192380.4295 | $ /ton NOx(R)
|  |  | 8305-02-02 |  |  | #N/A | 2: #N/A; 4: #N/A; 8: #N/A; 10: 2 | Combination of Control Technologies LNB + OFA + SNCR | #N/A |  |  | Combination of Control Technologies LNB + OFA + SNCR |  |  |  |  | Combination of Control Technologies LNB + OFA + SNCR
[6 empty] | #N/A | 2: #N/A; 4: #N/A; 8: #N/A
[6 empty] | #N/A | 2: #N/A; 4: #N/A; 8: #N/A | η ≈ 45% |  | 2 |  | η ≈ 45% | 0.152 lb/MMBtu | 5.3 |  |  | η ≈ 45% | 0.152 lb/MMBtu | 5.3
[6 empty] | #N/A | 2: #N/A; 4: #N/A; 8: #N/A | 5537165 | $ TCC/unit |  |  | 5537165 | $ TCC/unit | 415337.9785 |  |  | 5537165 | $ TCC/unit | 415337.9785
[6 empty] | #N/A | 2: #N/A; 4: #N/A; 8: #N/A | 32571.5588 | $ TCC / MW nominal capacity |  |  | 32571.5588 | $ TCC / MW nominal capacity |  |  |  | 32571.5588 | $ TCC / MW nominal capacity
[6 empty] | #N/A | 2: #N/A; 4: #N/A; 8: #N/A | 196596 | $ /ton NOx(R) |  |  | 78218.075 | $ /ton NOx(R) | (see note below) |  |  | 139233.3306 | $ /ton NOx(R)
|  |  | 8305-02-03 |  |  |  | 8: #N/A; 10: 3 | Combination of Control Technologies LNB + OFA + FGR | #N/A |  |  | Combination of Control Technologies LNB + OFA + FGR |  |  |  |  | Combination of Control Technologies LNB + OFA + FGR
#N/A
[7 empty] | 8: #N/A | η ≈ 45% |  | 1 |  | η ≈ 45% | 0.152 lb/MMBtu | 5.3 |  |  | η ≈ 45% | 0.152 lb/MMBtu | 5.3
[7 empty] | 8: #N/A | 4271527 | $ TCC/unit |  |  | 4271527 | $ TCC/unit | 320403.5619 |  |  | 4271527 | $ TCC/unit | 320403.5619
[7 empty] | 8: #N/A | 25126.6294 | $ TCC / MW nominal capacity |  |  | 25126.6294 | $ TCC / MW nominal capacity |  |  |  | 25126.6294 | $ TCC / MW nominal capacity
[7 empty] | 8: #N/A | 122660 | $ /ton NOx(R) |  |  | 60339.6539 | $ /ton NOx(R) | (see note below) |  |  | 111646.441 | $ /ton NOx(R)
8305-03 | PSEG | BHB3 | 8305-03-01 |  | 10 |  | 8305 | Bridgeport Harbor Station | BHB3 | 410 | 58 yrs | None | Coal; No. 6 oil | Work in progress, PSEG asks for more time to develop a solution, due to limited information on the NOx control technologies feasibility on coal boliers
[16 empty] | Unit NOx Rate - | lb/MMBtu |  |  | Unit NOx Rate - | lb/MMBtu |  |  |  | Unit NOx Rate - | lb/MMBtu
[16 empty] | Note: |  |  |  | Note: |  |  |  |  | Note:
[16 empty] | All Cost Effectiveness data, shown in Section I are per stakeholder report. Some stakeholders did not provide the yearly quantity of NOx(R) removed |  |  |  | Since no Annual Cost breakdown was provided, PSEG units Cost Effectiveness is based on the stakeholder Annual Cost data, only - changes in CR cannot be included in Cost Effectiveness calculation. |  |  |  |  | Some Section III, Cost Effectiveness Indicators may be higher vs. Section II, due using a leveled Total Annual Direct Costs for all TA&O units based on reports available data (esp. NRG)

## 3(lst)
Summary:
– Table 2 lists all 2010 active Trade Agreements & Orders (TA&O); There are 8 orders including 39 emission units
– Table 2 has three separate (horizontal) sections, respectively for:
● Combustion Turbines - List No's 1 through 14, including 27 emission units
● Diesel Engines - List No 15, including (2) two identical emission units
● Utility Boilers - List No's 16 through 25, including 10 emission units
– An ID number was assisgned to each emission unit - see nomenclature below
|  | XXXX | TA&O ID, a 4 digit registration number assigned by DEEP
|  | XXXX-YY | Emission Unit ID, a composite number derived from TA&O ID followed by a dash separator and a two digit sequencial number of all units listed withn a TA&O
|  | XXXX-YY-ZZ | NOx Control ID within for a designated emission unit, a composite number derived from unit ID, by adding a dash separator followed by a two digit sequencial number , uniques for each control analyzed.
Note:
List No's are hyperlinked to Emission Unit Record page. To see a unit record data, click on the unit's list number in the colum 1 below
x
LIST OF 2010 ACTIVE TRADING AGREMENTS & ORDERS
Table 2
| List No. | TA&O | Owner/Operator | Owner/Operator Name /Initials | Facility Name (per EPA CAIR Report) | NOx Emission Unit
[6 empty] | Unit Tag (per Operator and/or EPA CAIR Report) | Emission Unit Type | Nom. Power | No, Identical Units | Age | Fuel | ID
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
| 1 | 8298 | Capitol District Energy Center Cogeneration Associates | CDECCA | Capitol District Energy Center | GT | Combustion Turbine |  | 1 | 38 yrs | Natural Gas; No. 2 oil | 8298-01
| 2 | 8302 | Connecticut Resources Recovery Authority | CRRA | South Meadow Station | 11A |  | 40 | 8 | 57 yrs | Jet Fuel A (Kerosene K1); No. 2 oil | 8302-01
[5 empty] | South Meadow Station | 11B |  |  | 8 | 57 yrs | Jet Fuel A (Kerosene K1); No. 2 oil | 8302-02
[5 empty] | South Meadow Station | 12A |  | 40 | 8 | 57 yrs | Jet Fuel A (Kerosene K1); No. 2 oil | 8302-03
[5 empty] | South Meadow Station | 12B |  |  | 8 | 57 yrs | Jet Fuel A (Kerosene K1); No. 2 oil | 8302-04
[5 empty] | South Meadow Station | 13A |  | 40 | 8 | 57 yrs | Jet Fuel A (Kerosene K1); No. 2 oil | 8302-05
[5 empty] | South Meadow Station | 13B |  |  | 8 | 57 yrs | Jet Fuel A (Kerosene K1); No. 2 oil | 8302-06
[5 empty] | South Meadow Station | 14A |  | 40 | 8 | 57 yrs | Jet Fuel A (Kerosene K1); No. 2 oil | 8302-07
[5 empty] | South Meadow Station | 14B |  |  | 8 | 57 yrs | Jet Fuel A (Kerosene K1); No. 2 oil | 8302-08
| 3 | 8303 | FirstLight Hydro Generating Company | FirstLight | Tunnel | 10 |  | 20 | 1 | 58 yrs | Jet Fuel A (Kerosene K1); | 8303-01
| 4 | 8304 | Norwich Public Utilities | NPU | Norwich | TRBINE |  | 18.8 | 1 | 55 yrs | No. 2 oil; | 8304-01
| 5 | 8301 | PSEG Power LLC, PSEG Fossil LLC, PSEG Power Connecticut | PSEG | Bridgeport Harbor Station | BHB4 |  | 22 | 1 | 60 yrs | Jet Fuel A (Kerosene K1); | 8301-01
| 6 | 8300 | NRG Energy, Inc | NRG | Branford | BR10 | Combustion Turbine | 20 | 1 | 57 yrs | Ultra low sulfur kerosene oil (ULSD); | 8300-01
| 7 |  | 0 | NRG | Cos Cob | CC10 |  | 20 | 3 | 57 yrs | Ultra low sulfur kerosene oil (ULSD); | 8300-02
|  |  | 0 | NRG | Cos Cob | CC11 |  | 20 | 3 | 57 yrs | Ultra low sulfur kerosene oil (ULSD); | 8300-03
|  |  | 0 | NRG | Cos Cob | CC12 |  | 20 | 3 | 57 yrs | Ultra low sulfur kerosene oil (ULSD); | 8300-04
| 8 |  | 0 | NRG | Cos Cob | CC13 |  | 20 | 2 | 57 yrs | Ultra low sulfur kerosene oil (ULSD); Natural Gas | 8300-05
|  |  | 0 | NRG | Cos Cob | CC14 |  | 20 | 2 | 57 yrs | Ultra low sulfur kerosene oil (ULSD); Natural Gas | 8300-06
| 9 |  | 0 | NRG | Franklin Drive | FD10 |  | 20 | 1 | 58 yrs | Ultra low sulfur kerosene oil (ULSD); | 8300-07
| 10 |  | 0 | NRG | Torrington Terminal | TT10 |  | 20 | 1 | 58 yrs | Ultra low sulfur kerosene oil (ULSD); | 8300-08
| 11 |  | 0 | NRG | Middletown | MD10 |  | 20 | 1 | 60 yrs | Ultra low sulfur kerosene oil (ULSD); | 8300-09
| 12 |  | 0 | NRG | Norwalk Harbor Station | NH10 |  | 17 | 1 | 60 yrs | No.2 Oil; | 8300-10
| 13 |  | 0 | NRG | Devon | DV10 |  | 20 | 1 | 38 yrs | Ultra low sulfur kerosene oil (ULSD); | 8300-11
| 14 |  | 0 | NRG | Devon | DV11 |  | 40 | 4 | 30 yrs | ULSD oil; Natural Gas | 8300-12
| 0 |  | 0 | NRG | Devon | DV12 |  | 40 | 4 | 30 yrs | ULSD oil; Natural Gas | 8300-13
| 0 |  | 0 | NRG | Devon | DV13 |  | 40 | 4 | 30 yrs | ULSD oil; Natural Gas | 8300-14
| 0 |  | 0 | NRG | Devon | DV14 |  | 40 | 4 | 30 yrs | ULSD oil; Natural Gas | 8300-15 | 27
| 15 | 8300 | NRG Energy, Inc | NRG | Montville | MV10 | Diesel Engine | 2.75 | 2 | 61 yrs | 0.05% sulfur distillate oil; | 8300-16
| 0 |  | 0 | NRG | Montville | MV11 |  | 2.75 | 2 | 61 yrs | 0.05% sulfur distillate oil; | 8300-17 | 2
| 16 | 8306 | NRG Energy, Inc | NRG | Middletown | MD2 | Utility Boiler | 120 | 1 |  | No. 6 oil; No. 2 oil | 8306-01
| 17 | 8306 | 0 | NRG | Middletown | MD3 |  | 236 | 1 |  | No. 6 oil; No. 2 oil | 8306-02
| 18 | 8306 | 0 | NRG | Middletown | MD4 |  | 400 | 1 |  | No. 6 oil; No. 2 oil | 8306-03
| 19 | 8306 | NRG Energy, Inc | NRG | Montville | MV5 |  | 81 | 1 |  | No. 6 oil; Nat. Gas | 8306-04
| 20 | 8306 | 0 | NRG | Montville | MV6 |  | 402 | 1 |  | No. 6 oil; No. 2 oil | 8306-05
| 21 | 8306 | NRG Energy, Inc | NRG | Norwalk Harbor Station | NH1 |  | 164 | 1 |  | No. 6 oil; No. 2 oil | 8306-06
| 22 | 8306 | 0 | NRG | Norwalk Harbor Station | NH2 |  | 172 | 1 |  | No. 6 oil; No. 2 oil | 8306-07
| 23 | 8305 | PSEG Power LLC, PSEG Fossil LLC, PSEG Power Connecticut | PSEG | New Haven Harbor | NHB1 |  | Unit is a steam boiler, only | 1 | 52 yrs | No. 6 oil; | 8305-01
| 24 | 8305 | 0 | PSEG | Bridgeport Harbor Station | BHB2 |  | 170 | 1 | 66 yrs | No. 6 oil; No. 2 oil | 8305-02
| 25 | 8305 | 0 | PSEG | Bridgeport Harbor Station | BHB3 |  | 410 | 1 | 58 yrs | Coal; No. 6 oil | 8305-03 | 10
8
Formulas:
Owner/Operator = +IF([ID]="","",VLOOKUP(MATCH([ID],tid,0),tao,'12(id)'!$I20,FALSE()))

## 4(rd)
Summary:
|  |  |  | – | Form below allows to see the record data of any emission unit listed within the 2010 active TA&O(s)
|  |  |  | – | The record data include:
[5 empty] | ● | Emission unit DEEP registration records
[5 empty] | ● | Unit ID, Site location, Equipment Specification (Model, Manufacturer, Size, Fuel, Nominal Capacity, Age)
[5 empty] | ● | Unit's EPA CAIROS data for the last three years, 2010, 2009 and 2008
[5 empty] | ● | Unit emission rates, stack test, FLER and AEL
[5 empty] | ● | Stakeholder report NOx emission rates and annual NOx discharge considered for cost analysis
[5 empty] | ● | Stakeholder site condition assessment and proposed NOx control technology
|  |  |  | – | In order to see an emission unit record data, type the unit's listed number in the designated box below (cell C20)
[15 empty] | Facility: |  |  | South Meadow Station
|  |  | x | [11 empty] | ID: |  |  | 8302-01
[17 empty] | Revsion |  | 1
Enter here Emission | [16 empty] | Rev. Date |  | 2011-11-25
Unit's List No. ▬► |  | 2 | [6 empty] | TRADING AGREEMENT and ORDER
REFERENCE LIST NO's | [8 empty] | SOUTH MEADOW STATION
Owner Operator | Facility Tag | List No. | [6 empty] | CONNECTICUT RESOURCES RECOVERY AUTHORITY
CDECCA | GT | 1 | [6 empty] | EMISSION UNIT SPECIFICATIONS AND RECORD DATA
CRRA | 11A,B-14A,B | 2
FirstLight | 10 | 3 | [13 empty] | Today's Date: |  | 2026-08-06 00:56
NPU | TRBINE | 4
PSEG | BHB4 | 5 |  | Trading Agreement & Order No. |  |  |  |  | 8302
NRG | BR10 | 6 |  | TA&O Objective |  |  |  |  | NOx RACT Compliance |  |  | RCSA 22a-174-22c (CAIR)
| CC10-12 | 7 |  | Date Issued By DEP |  |  |  |  | 2010-04-29
| CC13-14 | 8 |  | Expiration Date |  |  |  |  | 2014-05-31
| FD10 | 9 |  | Time to Expiration: |  |  |  |  | -12 years -2 months
| TT10 | 10 |  | Prior TA&O No. |  |  |  |  | 8116B
| MD10 | 11 |  | Prior TA&O Issue Date:
| NH10 | 12
| DV10 | 13 |  | Title V Permit No.: |  |  |  |  | 075-0252-TV
| DV11-14 | 14 |  | Date Issued |  |  |  |  | 2006-11-20
| MV10-11 | 15 |  | Expiration: |  |  |  |  | 2011-11-20
NRG | MD2 | 16 |  | Client/Sequence/Town/Premises No's: |  |  |  |  | 5497 / 002 / 075 / 0158
| MD3 | 17
| MD4 | 18 |  | Owner |  |  |  |  | Connecticut Resources Recovery Authority
| MV5 | 19 |  | Ownership Starting Date (Year)
| MV6 | 20 |  | Approving TAO Official and Title |  |  |  |  | Peter W. Egan, Director of Environmental Affairs and Development
| NH1 | 21 |  | Operator (Company Name & Initials) |  |  |  |  | #VALUE!
| NH2 | 22 |  | Address: |  |  |  |  | 100 Constitution Plaza, 6th Floor, Hartford, CT 06103
PSEG | NHB1 | 23 |  | Name of Responsible Official and Title |  |  |  |  | Steven E. Yates, Air Compliance Manager
| BHB2 | 24 |  | Telephone /Email |  |  |  |  | (860) 757-7725
| BHB3 | 25
|  |  |  | Premises/Facility Name |  |  |  |  | South Meadow Station
|  |  |  | Facility ID (ORISPL) |  |  |  |  | 563 |  |  | Note: EPA NOx - CAIROS program listed
|  |  |  | Site |  |  |  |  | Reserve - Maxim Roads, Hartford
|  |  |  | Physical Address |  |  |  |  | 20 Reserve Rd Hartford, CT 06114
|  |  |  | Emission Units Group ID |  |  |  |  | GEU-1
|  |  |  | Group Name (per owner) |  |  |  |  | South Meadows Jets
|  |  |  | No (Identical) Emission Units |  |  |  |  | 8 Emission Units |  |  | 4 Twin-pack Modules
|  |  |  | Description: |  |  |  |  | Eight (four twin-packs) identical simple cycle gas turbine engine; two turbines per generator operating simultaneously, each turbine has its own stack
|  |  |  | TA&O Unit Registration Tag |  |  |  |  | 11A, 11B, 12A, 12B, 13A, 13B, 14A, 14B
|  |  |  | Operator's Tag |  |  | 11A, 11B, 12A, 12B, 13A, 13B, 14A, 14B | , | (same as above)
|  |  |  | Refer to: |  |  |  |  | Single turbine within a twin pack module
|  |  |  | DEEP Registration type |  |  |  |  | Registration
|  |  |  | DEEP Registration No. |  |  |  |  | R-075-0260, 261, 262, 263, 264, 265, 266, 267
Date Issued
|  |  |  | Expiration Date |  |  |  |  | None
|  |  |  | Equipmet Type/Make |  |  |  |  | Combustion Turbine
|  |  |  | Manufacturer: |  |  |  |  | Pratt & Whitney
|  |  |  | Model: |  |  |  |  | TP4-2(A9) LF
|  |  |  | Description: |  |  |  |  | Twin pack with two simple cycle turbines (A & B) running simultaneously
|  |  |  | Date of Installation: |  |  |  |  | 1970-01-01
|  |  |  | Equipment Age: |  |  |  |  | 57 years old |  |  | Note: | Limited aftermarket suppliers of parts
|  |  |  | Application |  |  |  |  | EGU |  |  | Unit Output: | Electric Services
|  |  |  | Notes: |  |  |  |  | Driven by turbines A and B operating simultaneously
|  |  |  | Generator Name Plate Specifications |  |  |  |  | 46,000 kVA, 0.9 PF, 13,800 V, 3 Phase, 60 Hz
|  |  |  | Power Capacity |  |  |  |  | Nominal |  |  | Summer Output (at 90ºF) | [5 empty] | Winter Output (at 90ºF)
[9 empty] | 40 MW |  |  | 19.3 MW | [5 empty] | 22.1 MW
|  |  |  | Note: |  |  |  |  | Per Twin-Pack module
|  |  |  | Facility Total Installed |  |  |  |  | 160 MW
Nominal BTU Capacity
|  |  |  | Fuel(s) per TA&O and Permit |  |  |  |  | Kerosene A, #2 and other oils
|  |  |  | Primary Fuel |  |  |  |  | Jet Fuel A (Kerosene K1) |  |  | per TitleV Permit & Operator's Report
|  |  |  | Fuel Rate |  |  |  |  | 1900 | gal/hr |  | per TitleV Permit
|  |  |  | Heat Input |  |  |  |  | 256 | MMBtu/hr |  | per TA&O
|  |  |  | Secodary Fuel |  |  |  |  | No. 2 oil |  |  | per TA&O
|  |  |  | Fuel Rate |  |  |  |  | 1900 | gal/hr
|  |  |  | Heat Input |  |  |  |  | 256 | MMBtu/hr |  | per TA&O
|  |  |  | Alternate Fuel |  |  |  |  | other distillate oil |  |  | per TA&O
|  |  |  | Fuel Rate |  |  |  |  | 1900 | gal/hr
|  |  |  | Heat Input |  |  |  |  | 256 | MMBtu/hr |  | per TA&O
|  |  |  | Emissions Tests |  |  |  |  | CEM |  |  | Date of Stack Test | [5 empty] | 2009-11-15
|  |  |  | Stack Test Rate |  |  |  |  | 0.675 | lb/MMBtu |  | Date of Next Stack Test | [5 empty] | 2014-11-15
|  |  |  | Stack Test Rate |  |  |  |  | 132.5 | ppmvd |  | Frequency | [5 empty] | 4.9993
|  |  |  | Full Load Emission Rate (FLER) |  |  |  |  | 0.81 | lb/MMBtu |  | Primary fuel
|  |  |  | Allowable Emission Limit (AEL) |  |  |  |  | 0.289 | lbs/MMBtu
[9 empty] | 75 | ppmvd
AEL non-ozone season
|  |  |  | Lowest target NOx AEL |  |  |  |  | 0.15 | lb/MMBtu | or | 40 |  | ppmvd
EPA's CAIROS REPORT SUMMARY
|  |  |  | Report Year |  |  |  |  | 2010 |  |  | 2009 | [5 empty] | 2008
|  |  |  | EPA OS Reported Operating Time |  |  |  |  | 19 | hours |  | 8 |  | hours |  |  |  | 12 | hours
|  |  |  | No. of Months Reported |  |  |  |  | 5 | months |  | 5 |  | months |  |  |  | 5 | months
|  |  |  | Gross Load |  |  |  |  | 285 | MWh |  | 78 |  | MWh |  |  |  | 126 | MWh
|  |  |  | Heat Input |  |  |  |  | 3819 | MMBtu |  | 1013 |  | MMBtu |  |  |  | 1575 | MMBtu
|  |  |  | Avg. NOx Rate (reported) |  |  |  |  | 0.78 | lbs/MMBtu |  | 0.78 |  | lbs/MMBtu |  |  |  | 0.78 | lbs/MMBtu
|  |  |  | Avg. NOx Rate (calculated) |  |  |  |  | 0.78555 | lbs/MMBtu |  | 0.78973 |  | lbs/MMBtu |  |  |  | 0.88889 | lbs/MMBtu
|  |  |  | NOx |  |  |  |  | 1.5 | tons/yr |  | 0.4 |  | tons/yr |  |  |  | 0.7 | tons/yr
|  |  |  | Fuel Type(s) (Primary)/per EPA report |  |  |  |  | Diesel Oil |  |  | Diesel Oil | [5 empty] | Diesel Oil
|  |  |  | Note: |  | Data above is per emission unit
Installed NOx Controls
(per EPA CAIROS Report)
OPERATOR ASSESSMENT REPORT
|  |  |  | Report Issued (Y/N) |  |  |  |  | Yes
|  |  |  | Company Issuing Report |  |  |  |  | Combustion Components Associates, Inc. (CCA)
|  |  |  | Telephone/Fax |  |  |  |  | (203) 268-3139 |  |  | (203) 261-7697
|  |  |  | Project No. |  |  |  |  | NU-SMEADOW-10-1 | [6 empty] | Rev: |  | Re-sent modified
|  |  |  | Report Date: |  |  |  |  | 2011-01-26 | [6 empty] | Date |  | 2011-04-29
|  |  |  | Prepared By |  |  |  |  | Howard A.S. Brooks and Edmund Schindler
|  |  |  | Report Objective: |  |  |  |  | Evaluate control technology options to reduce the current NOx level from 130 ppm to between 25 and 50 ppmvd at 15% oxygen
|  |  |  | Equipment Use |  |  |  |  | Emergency and DR with black start capability, running at full load of 160 MW (40MW/EGU) for 48 hrs, plus any additional time required by ISO-NE
|  |  |  | Equipment Existing Operating Controls |  |  |  |  | Modbus Modicon TSX Quantum per each EGU - for operation control
Equipment Existing NOx Controls
[5 empty] | ─ | Per Stakeholder Report |  |  | None
[5 empty] | ─ | Per EPA CAIROS Report
|  |  |  | Monitoring Controls |  |  |  |  | None
Report Year
Reported Annual Operating Time per unit
Ozone-Season Operating Time
Non-Ozone-Season Operating Time
Heat Input
MWH Generated
NOx Emission
Data Considered for Assessment
|  |  |  | Uncontrolled NOx rate |  |  |  |  | 0.7305 | lbs/MMBtu
[9 empty] | 129.3684 | ppmvd
Hours of Operation
NOx Emission
|  |  |  | Site Condition |  |  |  |  | Very compact, congested if adding new NOx reducing technology. Additional real estate and extensive civil engineering work to re-arrange the site will be needed. Existence of high-voltage power lines limit the available space for new equipment.
|  |  |  | Site Utilities Assesment |  |  |  |  | Existing fuel tank must be replaced by new smaller tanks. City water is available to supply 200-250 gpm for a new low NOx reduction equipment.
NOx Reduction Technologies Proposed by Stakeholder
|  |  |  | 1.- |  |  |  |  | Selective Catalytic Reduction (SCR)
|  |  |  | 2.- |  |  |  |  | HPWI + Ultra Low Sulfur Fuel
|  |  |  | 3.- |  |  |  |  | High Pressure Water Injection (HPWI)
|  |  |  | 4.- |  |  |  |  | Dry Low NOx Combustor - DLNC

## 5(em)
Summary:
[5 empty] | – | Table 3 includes EPA CAIROS Ozone Season Data for TA&O units recorded during 2010, 2009 and 2008. See Col. 29-40 (2010), Col. 41-52 (2009) and Col. 53-64 (2008) respectively
[5 empty] | – | Since some CAIROS records indicated a default NOx rate of 1.20 lb/MMBtu (or > 1.00 lb/MMBtu) these records were replaced by Stack Test Data (see columns highlighted in light yellow)
[5 empty] | – | Each annual section includes also a column with NOx tons estimated based on Heat Input formula
[5 empty] | – | For each emission unit NOx data had been sorted and selected only the maximum yearly values among identical units and during the 3-years period (2010-2008) - Col. 74-102
[5 empty] | – | Table represents the data source for the plots on Page 6 (gph)
x
TA&O UNITS EPA CAIROS NOx EMISSIONS DATA (OZONE SEASON) |  |  |  |  | TA&O UNITS EPA CAIROS NOx EMISSIONS DATA (OZONE SEASON) | [71 empty] | UNCONTROLLED NOx - MAX PER YEAR AND PER IDENTICAL UNITS (COMBINED)
[18 empty] | Table 3 | [17 empty] | NOx tons/os = Heat Input x NOx Rate/2000 |  |  |  | 2010 | [11 empty] | 2009 | [11 empty] | 2008 | [42 empty] | Table 3
|  |  |  | No. | Seq. | ID | Owner/Operator | TAO | TA&O ID | Premises/Facility Name | DEP Registration | Tag | Nom. Power Capacity | Facility Total Power Installed | Application | Mfg | Model | Date of Mfg | Age | Existing NOx Controls per Stakeholder | Primary Fuel | Secondary Fuel | Heat Input (per TA&O) | Stack Test Rate | Stack Test Rate | FLER | Emission Rate Notes | Referenced Emission Rate by Stakeholder |  | Avg Op. Time/yr | NOx | CAIROS - OZONE SEASON 2010 | [11 empty] | CAIROS - OZONE SEASON 2009 | [11 empty] | CAIROS - OZONE SEASON 2008 | [11 empty] | EXISTING CONTROLS PER EPA CAIROS REPORT |  |  |  |  | CAIROS Max. Heat Input Capacity |  | NOx emissions rate (3-year average) |  | 2010 | [6 empty] | 2009 | [6 empty] | 2008 | [6 empty] | MAX over 3 yrs period | [7 empty] | 50 | REMARKS
[32 empty] | Year | EPA Reported Operating Time | No. of Months Reported | Gross Load | Avg. NOx Rate | NOx Tons | Avg. NOx Rate Selected | NOx Tons Estim | NOx/MWh | Heat Input | Fuel Type(s) (Primary) | Fuel Type(s) (Secondary) | Year | EPA Reported Operating Time | No. of Months Reported | Gross Load | Avg. NOx Rate | NOx Tons | Avg. NOx Rate Selected | NOx Tons Estim | NOx/MWh | Heat Input | Fuel Type(s) (Primary) | Fuel Type(s) (Secondary) | Year | EPA Reported Operating Time | No. of Months Reported | Gross Load | Avg. NOx Rate | NOx Tons | Avg. NOx Rate Selected | NOx Tons Estim | NOx/MWh | Heat Input | Fuel Type(s) (Primary) | Fuel Type(s) (Secondary) | NOx Controls 01 | NOx Controls 02 | NOx Controls 03 | SO₂ Controls | PM Controls |  |  |  |  | Operating Time (Ozone season) | Gross Load (MWh) | Heat Input | NOx Tons | Avg. NOx Rate Selected | Avg. NOx Rate Clc | NOx Rate (hourly) | Operating Time (Ozone season) | Gross Load (MWh) | Heat Input | NOx Tons | Avg. NOx Rate Selected | Avg. NOx Rate Clc | NOx Rate (hourly) | Operating Time (Ozone season) | Gross Load (MWh) | Heat Input | NOx Tons | Avg. NOx Rate Selected | Avg. NOx Rate Clc | NOx Rate (hourly) | Year Recorded | Operating Time (Ozone season) | Gross Load | Heat Input | NOx Tons Estim | NOx Rate | NOx Rate clc=ton/HI | NOx Rate (hourly) | 50 hrs max NOx tons estim
[23 empty] | MMBtu/hr | lbs/MMBtu | ppmvd | lbs/MMBtu |  | lbs/MMBtu | ppmvd | hrs/yr | ton/yr |  | hrs | mths | MWh | lb/MMBtu | ton/yr | lb/MMBtu | ton/yr | grams/MWh | MMBtu |  |  |  | hrs | mths | MWh | lb/MMBtu | ton/yr | lb/MMBtu | ton/yr | grams/MWh | MMBtu |  |  |  | hrs | mths | MWh | lb/MMBtu | ton/yr | lb/MMBtu | ton/yr | grams/MWh | MMBtu | [7 empty] | MMBtu/hr |  | lb/MMBtu |  | hrs | MWh | MMBtu | tons/yr | lb/MMBtu | lb/MMBtu | lb/MMBtu/hr | hrs | MWh | MMBtu | tons/yr | lb/MMBtu | lb/MMBtu | lb/MMBtu/hr | hrs | MWh | MMBtu | tons/yr | lb/MMBtu | lb/MMBtu | lb/MMBtu/hr |  | hrs | MWh | MMBtu | tons/yr | lbm/MMBtu | lbm/MMBtu | lb/MMBtu/hr | tons/yr
REFERENCE ID |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104
8298-01 | CDECCA | GT |  | 1 | 1 | 1 | Capitol District Energy Center Cogeneration Associates | 8298 | 8298-01 | Capitol District Energy Center | Capital District Energy | GT |  |  | Combustion Turbine | General Electric | PG 6531 |  | 38 |  | Natural Gas | No. 2 oil | [9 empty] | 2010 | 229 | 5 | 8884 | 0.12 | 4.2 | 0.12 | 4.2 | 472.76 | 79936 | Pipeline Natural Gas | Diesel Oil | 2009 | 152 | 5 | 5669 | 0.12 | 2.7 | 0.12 | 2.7 | 476.2745 | 49960 | Pipeline Natural Gas | Diesel Oil | 2008 | 324 | 5 | 14379 | 0.12 | 7.2 | 0.12 | 7.2 | 500.7302 | 128717 | Pipeline Natural Gas | Diesel Oil | [5 empty] | 739 |  | 483.2549 |  | 229 | 8884 | 79936 | 4.2 | 0.12 | 0.10508 | 0.00045888 | 152 | 5669 | 49960 | 2.7 | 0.12 | 0.10809 | 0.0007111 | 324 | 14379 | 128717 | 7.2 | 0.12 | 0.11187 | 0.00034529 | 2008 | 324 | 14379 | 128717 | 7.2 | 0.12 | 0.112 | 0.022222 | 1.1111
8302-01 | CRRA | 11A |  | 2 | 2 | 2 | Connecticut Resources Recovery Authority | 8302 | 8302-01 | South Meadow Station | 11A | 11A | 40 | 160 | Combustion Turbine | Pratt & Whitney | TP4-2(A9) LF | 1970 | 57 | None | Jet Fuel A (Kerosene K1) | No. 2 oil | 256 | 0.675 | 132.5 | 0.81 |  | 0.675 | 132.5 |  |  | 2010 | 15 | 5 | 221 | 0.75 | 1.1 | 0.75 | 1.1 | 4977.3756 | 2925 | Diesel Oil |  | 2009 | 8 | 5 | 68 | 0.85 | 0.4 | 0.85 | 0.4 | 5882.3529 | 869 | Diesel Oil |  | 2008 | 12 | 5 | 126 | 0.83 | 0.7 | 0.83 | 0.7 | 5555.5556 | 1575 | Diesel Oil | [6 empty] | 266 |  | 5471.7614 |  | 19 | 285 | 3819 | 1.5 | 0.78 | 0.78555 | 0.041345 | 8 | 78 | 1013 | 0.4 | 0.78 | 0.78973 | 0.098717 | 12 | 126 | 1575 | 0.7 | 0.78 | 0.88889 | 0.074074 | 2010 | 19 | 285 | 3819 | 1.5 | 0.78 | 0.786 | 0.078947 | 3.9474
8302-02 | 0 | 11B |  | 1: 3; 2: 3; 5: 8302; 6: 8302-02; 7: South Meadow Station; 8: 11B; 9: 11B; 12: Combustion Turbine; 13: Pratt & Whitney; 14: TP4-2(A9) LF; 15: 1970; 16: 57; 17: None; 18: Jet Fuel A (Kerosene K1); 19: No. 2 oil; 20: 256; 21: 0.71; 22: 138.4; 23: 0.81; 25: 0.71; 26: 138.4; 29: 2010; 30: 15; 31: 5; 32: 221; 33: 0.76; 34: 1.1; 35: 0.76; 36: 1.1; 37: 4977.3756; 38: 2925; 39: Diesel Oil; 41: 2009; 42: 8; 43: 5; 44: 68; 45: 0.75; 46: 0.3; 47: 0.75; 48: 0.3; 49: 4411.7647; 50: 869; 51: Diesel Oil; 53: 2008; 54: 12; 55: 5; 56: 126; 57: 0.73; 58: 0.6; 59: 0.73; 60: 0.6; 61: 4761.9048; 62: 1575; 63: Diesel Oil; 70: 266; 72: 4717.015; 99: 0
8302-03 | 0 | 12A |  | 1: 4; 2: 4; 5: 8302; 6: 8302-03; 7: South Meadow Station; 8: 12A; 9: 12A; 10: 40; 12: Combustion Turbine; 13: Pratt & Whitney; 14: TP4-2(A9) LF; 15: 1970; 16: 57; 17: None; 18: Jet Fuel A (Kerosene K1); 19: No. 2 oil; 20: 256; 21: 0.744; 22: 124.8; 23: 0.81; 25: 0.744; 26: 124.8; 29: 2010; 30: 19; 31: 5; 32: 285; 33: 0.8; 34: 1.5; 35: 0.8; 36: 1.5; 37: 5263.1579; 38: 3819; 39: Diesel Oil; 41: 2009; 42: 7; 43: 5; 44: 78; 45: 0.82; 46: 0.4; 47: 0.82; 48: 0.4; 49: 5128.2051; 50: 1013; 51: Diesel Oil; 53: 2008; 54: 11; 55: 5; 56: 123; 57: 0.8; 58: 0.6; 59: 0.8; 60: 0.6; 61: 4878.0488; 62: 1560; 63: Diesel Oil; 70: 266; 72: 5089.8039; 99: 0
8302-04 | 0 | 12B |  | 1: 5; 2: 5; 5: 8302; 6: 8302-04; 7: South Meadow Station; 8: 12B; 9: 12B; 12: Combustion Turbine; 13: Pratt & Whitney; 14: TP4-2(A9) LF; 15: 1970; 16: 57; 17: None; 18: Jet Fuel A (Kerosene K1); 19: No. 2 oil; 20: 256; 21: 0.706; 22: 114.8; 23: 0.81; 25: 0.706; 26: 114.8; 29: 2010; 30: 19; 31: 5; 32: 285; 33: 0.76; 34: 1.5; 35: 0.76; 36: 1.5; 37: 5263.1579; 38: 3819; 39: Diesel Oil; 41: 2009; 42: 7; 43: 5; 44: 78; 45: 0.74; 46: 0.4; 47: 0.74; 48: 0.4; 49: 5128.2051; 50: 1013; 51: Diesel Oil; 53: 2008; 54: 11; 55: 5; 56: 123; 57: 0.72; 58: 0.6; 59: 0.72; 60: 0.6; 61: 4878.0488; 62: 1560; 63: Diesel Oil; 70: 266; 72: 5089.8039; 99: 0
8302-05 | 0 | 13A |  | 1: 6; 2: 6; 5: 8302; 6: 8302-05; 7: South Meadow Station; 8: 13A; 9: 13A; 10: 40; 12: Combustion Turbine; 13: Pratt & Whitney; 14: TP4-2(A9) LF; 15: 1970; 16: 57; 17: None; 18: Jet Fuel A (Kerosene K1); 19: No. 2 oil; 20: 256; 21: 0.75; 22: 132.5; 23: 0.81; 25: 0.75; 26: 132.5; 29: 2010; 30: 18; 31: 5; 32: 248; 33: 0.81; 34: 1.4; 35: 0.81; 36: 1.4; 37: 5645.1613; 38: 3313; 39: Diesel Oil; 41: 2009; 42: 8; 43: 5; 44: 72; 45: 0.86; 46: 0.4; 47: 0.86; 48: 0.4; 49: 5555.5556; 50: 910; 51: Diesel Oil; 53: 2008; 54: 12; 55: 5; 56: 111; 57: 0.88; 58: 0.6; 59: 0.88; 60: 0.6; 61: 5405.4054; 62: 1405; 63: Diesel Oil; 70: 266; 72: 5535.3741; 99: 0
8302-06 | 0 | 13B |  | 1: 7; 2: 7; 5: 8302; 6: 8302-06; 7: South Meadow Station; 8: 13B; 9: 13B; 12: Combustion Turbine; 13: Pratt & Whitney; 14: TP4-2(A9) LF; 15: 1970; 16: 57; 17: None; 18: Jet Fuel A (Kerosene K1); 19: No. 2 oil; 20: 256; 21: 0.733; 22: 130.3; 23: 0.81; 25: 0.733; 26: 130.3; 29: 2010; 30: 18; 31: 5; 32: 248; 33: 0.79; 34: 1.3; 35: 0.79; 36: 1.3; 37: 5241.9355; 38: 3313; 39: Diesel Oil; 41: 2009; 42: 8; 43: 5; 44: 72; 45: 0.82; 46: 0.4; 47: 0.82; 48: 0.4; 49: 5555.5556; 50: 910; 51: Diesel Oil; 53: 2008; 54: 12; 55: 5; 56: 111; 57: 0.84; 58: 0.6; 59: 0.84; 60: 0.6; 61: 5405.4054; 62: 1405; 63: Diesel Oil; 70: 266; 72: 5400.9655; 99: 0
8302-07 | 0 | 14A |  | 1: 8; 2: 8; 5: 8302; 6: 8302-07; 7: South Meadow Station; 8: 14A; 9: 14A; 10: 40; 12: Combustion Turbine; 13: Pratt & Whitney; 14: TP4-2(A9) LF; 15: 1970; 16: 57; 17: None; 18: Jet Fuel A (Kerosene K1); 19: No. 2 oil; 20: 256; 21: 0.755; 22: 124; 23: 0.81; 25: 0.755; 26: 124; 29: 2010; 30: 16; 31: 5; 32: 220; 33: 0.82; 34: 1.2; 35: 0.82; 36: 1.2; 37: 5454.5455; 38: 2931; 39: Diesel Oil; 41: 2009; 42: 6; 43: 5; 44: 64; 45: 0.86; 46: 0.4; 47: 0.86; 48: 0.4; 49: 6250; 50: 825; 51: Diesel Oil; 53: 2008; 54: 9; 55: 5; 56: 89; 57: 0.87; 58: 0.5; 59: 0.87; 60: 0.5; 61: 5617.9775; 62: 1135; 63: Diesel Oil; 70: 266; 72: 5774.1743; 99: 0
8302-08 | 0 | 14B |  | 1: 9; 2: 9; 5: 8302; 6: 8302-08; 7: South Meadow Station; 8: 14B; 9: 14B; 12: Combustion Turbine; 13: Pratt & Whitney; 14: TP4-2(A9) LF; 15: 1970; 16: 57; 17: None; 18: Jet Fuel A (Kerosene K1); 19: No. 2 oil; 20: 256; 21: 0.771; 22: 136.1; 23: 0.81; 25: 0.771; 26: 136.1; 29: 2010; 30: 16; 31: 5; 32: 220; 33: 0.84; 34: 1.2; 35: 0.84; 36: 1.2; 37: 5454.5455; 38: 2931; 39: Diesel Oil; 41: 2009; 42: 6; 43: 5; 44: 64; 45: 0.73; 46: 0.3; 47: 0.73; 48: 0.3; 49: 4687.5; 50: 825; 51: Diesel Oil; 53: 2008; 54: 9; 55: 5; 56: 89; 57: 0.74; 58: 0.4; 59: 0.74; 60: 0.4; 61: 4494.382; 62: 1135; 63: Diesel Oil; 70: 266; 72: 4878.8092; 99: 0
8303-01 | FirstLight | 10 |  | 10 | 10 | 3 | FirstLight Hydro Generating Company | 8303 | 8303-01 | Tunnel | Tunnel Road Preston 10 | 10 | 20 | 20 | Combustion Turbine | Pratt & Whitney | FT4-8 | Jan 1969 | 58 | None | Jet Fuel A (Kerosene K1) |  | NA | 0.698 | 119.6 | 0.72 |  | 0.698 | 119.6 | 50 | 4.5816 | 2010 | 20 | 5 | 301 | 0.73 | 1.7 | 0.73 | 1.7 | 5647.8405 | 4575 | Diesel Oil |  | 2009 | 3 | 5 | 46 | 0.79 | 0.3 | 0.79 | 0.3 | 6521.7391 | 808 | Diesel Oil |  | 2008 | 15 | 5 | 153 | 0.74 | 1 | 0.74 | 1 | 6535.9477 | 2596 | Diesel Oil | [6 empty] | 243 |  | 6235.1758 |  | 20 | 301 | 4575 | 1.7 | 0.73 | 0.74317 | 0.037158 | 3 | 46 | 808 | 0.3 | 0.79 | 0.74257 | 0.24752 | 15 | 153 | 2596 | 1 | 0.74 | 0.77042 | 0.051361 | 2010 | 20 | 301 | 4575 | 1.7 | 0.73 | 0.743 | 0.085 | 4.25
8304-01 | NPU | TRBINE |  | 11 | 11 | 4 | Norwich Public Utilities | 8304 | 8304-01 | Norwich | Rolls Royce Turbine | TRBINE | 18.8 | 18.8 | Combustion Turbine | Rolls Royce | Olympus B | 1972 | 55 | None | No. 2 oil |  | 249 | 0.553 | 141.31 | 0.62 |  | 0.553 | 141.31 | 50 | 2.7374 | 2010 | 19 | 5 | 327 | 0.62 | 1.5 | 0.62 | 1.5 | 4587.156 | 4811 | Diesel Oil |  | 2009 | 15 | 5 | 225 | 0.62 | 1.2 | 0.62 | 1.2 | 5333.3333 | 3782 | Diesel Oil |  | 2008 | 10 | 5 | 151 | 0.57 | 0.7 | 0.57 | 0.7 | 4635.7616 | 2595 | Diesel Oil | [6 empty] | 249 |  | 4852.0836 |  | 19 | 327 | 4811 | 1.5 | 0.62 | 0.62357 | 0.03282 | 15 | 225 | 3782 | 1.2 | 0.62 | 0.63458 | 0.042306 | 10 | 151 | 2595 | 0.7 | 0.57 | 0.5395 | 0.05395 | 2010 | 19 | 327 | 4811 | 1.5 | 0.62 | 0.624 | 0.078947 | 3.9474
8301-01 | PSEG | BHB4 |  | 12 | 12 | 5 | PSEG Power LLC, PSEG Fossil LLC, PSEG Power Connecticut | 8301 | 8301-01 | Bridgeport Harbor Station | Bridgeport Harbor Station (BHS) Unit No. 4 | BHB4 | 22 | 22 | Combustion Turbine | Pratt & Whitney | FT-4A-8LI | Jan 1967 | 60 | None | Jet Fuel A (Kerosene K1) |  | 287 | 0.709 | 186.17 | 0.73 |  | 0.709 | 186.17 |  |  | 2010 | 11 | 5 | 114 | 0.71 | 0.7 | 0.71 | 0.7 | 6140.3509 | 2026 | Other Oil |  | 2009 | 8 | 5 | 119 | 0.67 | 0.7 | 0.67 | 0.7 | 5882.3529 | 1962 | Other Oil |  | 2008 | 24 | 5 | 105 | 0.67 | 0.8 | 0.67 | 0.8 | 7619.0476 | 2366 | Other Oil | [6 empty] | 287 |  | 6547.2505 |  | 11 | 114 | 2026 | 0.7 | 0.71 | 0.69102 | 0.06282 | 8 | 119 | 1962 | 0.7 | 0.67 | 0.71356 | 0.089195 | 24 | 105 | 2366 | 0.8 | 0.67 | 0.67625 | 0.028177 | 2008 | 24 | 105 | 2366 | 0.8 | 0.67 | 0.676 | 0.033333 | 1.6667
8300-01 | NRG | BR10 |  | 13 | 13 | 6 | NRG Energy, Inc | 8300 | 8300-01 | Branford | Boston Post Road Branford -10 | BR10 | 20 | 20 | Combustion Turbine | Pratt & Whitney | FT4-A8 | Jul 1969 | 57 | None, per NRG report; Water Injection since Jun 2008 per EPA. | Ultra low sulfur kerosene oil (ULSD) |  | 256 | 0.726 |  | 0.8 |  | 0.726 |  | 29 | 3.4 | 2010 | 39 | 5 | 512 | 1.2 | 5.9 | 0.726 | 3.5393 | 6912.5977 | 9750 | Other Oil |  | 2009 | 2 | 5 | 20 | 1.2 | 0.3 | 0.726 | 0.19057 | 9528.75 | 525 | Other Oil |  | 2008 | 7 | 5 | 123 | 1.2 | 1.1 | 0.726 | 0.64541 | 5247.2683 | 1778 | Other Oil |  | Water Injection |  |  |  |  | 250 |  | 7229.5386 |  | 39 | 512 | 9750 | 3.5393 | 0.726 | 0.726 | 0.018615 | 2 | 20 | 525 | 0.19057 | 0.726 | 0.726 | 0.363 | 7 | 123 | 1778 | 0.64541 | 0.726 | 0.726 | 0.10371 | 2010 | 39 | 512 | 9750 | 3.5393 | 0.726 | 0.726 | 0.09075 | 4.5375
8300-02 |  | CC10 |  | 14 | 14 | 7 |  | 8300 | 8300-02 | Cos Cob | Sound Shore Drive Greenwich-10 | CC10 | 20 | 100 | Combustion Turbine | Pratt & Whitney | FT4-A9 | 1969 | 57 | Water Injection | Ultra low sulfur kerosene oil (ULSD) |  | 256 | 0.192 |  | 0.22 |  | 0.192 |  |  |  | 2010 | 44 | 5 | 677 | 1.2 | 6.6 | 0.192 | 1.0596 | 1565.2112 | 11038 | Other Oil |  | 2009 | 8 | 5 | 139 | 1.2 | 1.2 | 0.192 | 0.18893 | 1359.1942 | 1968 | Other Oil |  | 2008 | 11 | 5 | 183 | 1.2 | 1.6 | 0.192 | 0.26304 | 1437.377 | 2740 | Other Oil |  | Water Injection |  |  |  |  | 250 |  | 1453.9275 |  | 51 | 790 | 12848 | 1.2463 | 0.194 | 0.194 | 0.0038039 | 8 | 139 | 1968 | 0.18893 | 0.192 | 0.192 | 0.024 | 11 | 183 | 2740 | 0.26304 | 0.192 | 0.192 | 0.017455 | 2010 | 51 | 790 | 12848 | 1.2463 | 0.194 | 0.194 | 0.024436 | 1.2218
8300-03 |  | CC11 |  | 1: 15; 2: 15; 5: 8300; 6: 8300-03; 7: Cos Cob; 8: Sound Shore Drive Greenwich-11; 9: CC11; 10: 20; 12: Combustion Turbine; 13: Pratt & Whitney; 14: FT4-A9; 15: 1969; 16: 57; 17: Water Injection; 18: Ultra low sulfur kerosene oil (ULSD); 20: 256; 21: 0.185; 23: 0.22; 25: 0.185; 29: 2010; 30: 40; 31: 5; 32: 619; 33: 1.2; 34: 6.1; 35: 0.185; 36: 0.93286; 37: 1507.0477; 38: 10085; 39: Other Oil; 41: 2009; 42: 6; 43: 5; 44: 102; 45: 1.2; 46: 0.9; 47: 0.185; 48: 0.13551; 49: 1328.5539; 50: 1465; 51: Other Oil; 53: 2008; 54: 9; 55: 5; 56: 160; 57: 1.2; 58: 1.3; 59: 0.185; 60: 0.20581; 61: 1286.3281; 62: 2225; 63: Other Oil; 65: Water Injection; 70: 250; 72: 1373.9766; 99: 0
8300-04 |  | CC12 |  | 1: 16; 2: 16; 5: 8300; 6: 8300-04; 7: Cos Cob; 8: Sound Shore Drive Greenwich-12; 9: CC12; 10: 20; 12: Combustion Turbine; 13: Pratt & Whitney; 14: FT4-A9; 15: 1969; 16: 57; 17: Water Injection; 18: Ultra low sulfur kerosene oil (ULSD); 20: 256; 21: 0.194; 23: 0.22; 25: 0.194; 29: 2010; 30: 51; 31: 5; 32: 790; 33: 1.2; 34: 7.7; 35: 0.194; 36: 1.2463; 37: 1577.5392; 38: 12848; 39: Other Oil; 41: 2009; 42: 7; 43: 5; 44: 131; 45: 1.2; 46: 1.1; 47: 0.194; 48: 0.17266; 49: 1318.0153; 50: 1780; 51: Other Oil; 53: 2008; 54: 6; 55: 5; 56: 115; 57: 1.2; 58: 1; 59: 0.194; 60: 0.15471; 61: 1345.3478; 62: 1595; 63: Other Oil; 65: Water Injection; 70: 250; 72: 1413.6341; 99: 0
8300-05 |  | CC13 |  | 17 | 17 | 8 |  | 8300 | 8300-05 | Cos Cob | Sound Shore Drive Greenwich-13 | CC13 | 20 |  | Combustion Turbine | Pratt & Whitney | FT4-A9 | 1969 | 57 | Water Injection | Ultra low sulfur kerosene oil (ULSD) | Natural Gas | 256 | 0.194 |  | 0.22 |  | 0.194 |  |  |  | 2010 | 35 | 5 | 476 | 1.2 | 6.5 | 0.194 | 1.0507 | 2207.3613 | 10832 | Other Oil |  | 2009 | 8 | 5 | 155 | 1.2 | 1.6 | 0.194 | 0.25239 | 1628.3484 | 2602 | Other Oil |  | 2008 | 4 | 5 | 93 | 1.2 | 0.8 | 0.194 | 0.1327 | 1426.8387 | 1368 | Other Oil |  | Water Injection |  |  |  |  | 308 |  | 1754.1828 |  | 35 | 476 | 10832 | 1.0507 | 0.194 | 0.194 | 0.0055429 | 13 | 209 | 4118 | 0.35209 | 0.171 | 0.171 | 0.013154 | 4 | 93 | 1368 | 0.1327 | 0 | 0.194 | 0.0485 | 2010 | 35 | 476 | 10832 | 1.0507 | 0.194 | 0.194 | 0.03002 | 1.501
8300-06 |  | CC14 |  | 1: 18; 2: 18; 5: 8300; 6: 8300-06; 7: Cos Cob; 8: Sound Shore Drive Greenwich-14; 9: CC14; 10: 20; 12: Combustion Turbine; 13: Pratt & Whitney; 14: FT4-A9; 15: 1969; 16: 57; 17: Water Injection; 18: Ultra low sulfur kerosene oil (ULSD); 19: Natural Gas; 20: 256; 21: 0.171; 23: 0.22; 25: 0.171; 29: 2010; 30: 42; 31: 5; 32: 604; 33: 1.2; 34: 7.8; 35: 0.171; 36: 1.1087; 37: 1835.5604; 38: 12967; 39: Other Oil; 41: 2009; 42: 13; 43: 5; 44: 209; 45: 1.2; 46: 2.5; 47: 0.171; 48: 0.35209; 49: 1684.6364; 50: 4118; 51: Other Oil; 53: 2008; 54: 4; 55: 5; 56: 91; 57: 1.2; 58: 0.8; 59: 0.171; 60: 0.11406; 61: 1253.3736; 62: 1334; 63: Other Oil; 65: Water Injection; 70: 308; 72: 1591.1901; 99: 0
8300-07 |  | FD10 |  | 19 | 19 | 9 |  | 8300 | 8300-07 | Franklin Drive | Franklin Drive Torrington-10 | FD10 | 20 | 20 | Combustion Turbine | Pratt & Whitney | FT4-A8 | Jan 1969 | 58 | None | Ultra low sulfur kerosene oil (ULSD) |  | 256 | 0.76 |  | 0.8 |  | 0.76 |  | 38.8 | 4.2 | 2010 | 46 | 5 | 639 | 1.2 | 6.9 | 0.76 | 4.3757 | 6847.7308 | 11515 | Other Oil |  | 2009 | 5 | 5 | 62 | 1.2 | 0.7 | 0.76 | 0.4351 | 7017.7419 | 1145 | Other Oil |  | 2008 | 8 | 5 | 142 | 1.2 | 1.2 | 0.76 | 0.7828 | 5512.6761 | 2060 | Other Oil | [6 empty] | 250 |  | 6459.3829 |  | 46 | 639 | 11515 | 4.3757 | 0.76 | 0.76 | 0.016522 | 5 | 62 | 1145 | 0.4351 | 0.76 | 0.76 | 0.152 | 8 | 142 | 2060 | 0.7828 | 0.76 | 0.76 | 0.095 | 2010 | 46 | 639 | 11515 | 4.3757 | 0.76 | 0.76 | 0.095124 | 4.7562
8300-08 |  | TT10 |  | 20 | 20 | 10 |  | 8300 | 8300-08 | Torrington Terminal | South Main Street Torrington-10 | TT10 | 20 | 20 | Combustion Turbine | Pratt & Whitney | FT4-A8 | Jan 1969 | 58 | None | Ultra low sulfur kerosene oil (ULSD) |  | 256 | 0.68 |  | 0.8 |  | 0.68 |  | 29.5 | 3.2 | 2010 | 36 | 5 | 468 | 1.2 | 5.4 | 0.68 | 3.0838 | 6589.3162 | 9070 | Other Oil |  | 2009 | 6 | 5 | 91 | 1.2 | 0.8 | 0.68 | 0.47872 | 5260.6593 | 1408 | Other Oil |  | 2008 | 6 | 5 | 111 | 1.2 | 0.9 | 0.68 | 0.493 | 4441.4414 | 1450 | Other Oil | [6 empty] | 250 |  | 5430.4723 |  | 36 | 468 | 9070 | 3.0838 | 0.68 | 0.68 | 0.018889 | 6 | 91 | 1408 | 0.47872 | 0.68 | 0.68 | 0.11333 | 6 | 111 | 1450 | 0.493 | 0.68 | 0.68 | 0.11333 | 2010 | 36 | 468 | 9070 | 3.0838 | 0.68 | 0.68 | 0.085661 | 4.2831
8300-09 |  | MD10 |  | 21 | 21 | 11 |  | 8300 | 8300-09 | Middletown | Middletown-10 | MD10 | 20 | 953 | Combustion Turbine | Pratt & Whitney | FT4-A8 | Aug 1966 | 60 | None | Ultra low sulfur kerosene oil (ULSD) |  | 256 | 0.57 |  | 0.67 |  | 0.57 |  | 99.9 | 6.2 | 2010 | 95 | 5 | 1275 | 1.2 | 14.3 | 0.57 | 6.7687 | 5308.8235 | 23750 | Other Oil |  | 2009 | 20 | 5 | 243 | 1.2 | 3 | 0.57 | 1.4287 | 5879.4444 | 5013 | Other Oil |  | 2008 | 17 | 5 | 405 | 1.2 | 2.6 | 0.57 | 1.2112 | 2990.7407 | 4250 | Other Oil | [6 empty] | 250 |  | 4726.3362 |  | 95 | 1275 | 23750 | 6.7687 | 0.57 | 0.57 | 0.006 | 20 | 243 | 5013 | 1.4287 | 0.57 | 0.57 | 0.0285 | 17 | 405 | 4250 | 1.2112 | 0.57 | 0.57 | 0.033529 | 2010 | 95 | 1275 | 23750 | 6.7687 | 0.57 | 0.57 | 0.07125 | 3.5625
8300-10 |  | NH10 |  | 22 | 22 | 12 |  | 8300 | 8300-10 | Norwalk Harbor Station | Norwalk-10 | NH10 | 17 | 353 | Combustion Turbine | Westinghouse | W191 | Oct 1966 | 60 | None | No.2 Oil |  | 256 | 0.514 |  | 0.52 |  | 0.514 |  | 14.5 | 1 | 2010 | 21 | 5 | 204 | 1.17 |  | 0.514 | 1.246 | 6107.8581 | 4848.2609 | Other Oil |  | 2009 | 6 | 5 | 55 | 1.17 |  | 0.514 | 0.43124 | 7840.678 | 1677.9661 | Other Oil |  | 2008 | 8 | 5 | 67 | 1.18 | 0.3 | 0.514 | 0.52483 | 7833.2155 | 2042.1223 | Other Oil | [6 empty] | 232 |  | 7260.5838 |  | 21 | 204 | 4848.2609 | 1.246 | 0.514 | 0.514 | 0.024476 | 6 | 55 | 1677.9661 | 0.43124 | 0.514 | 0.514 | 0.085667 | 8 | 67 | 2042.1223 | 0.52483 | 0.514 | 0.514 | 0.06425 | 2010 | 21 | 204 | 4848.2609 | 1.246 | 0.514 | 0.514 | 0.059333 | 2.9667 | based on NRG Heat Input for 2010,209 and 2008
8300-11 |  | DV10 |  | 23 | 23 | 13 |  | 8300 | 8300-11 | Devon | Devon-10 | DV10 | 20 | 180 | Combustion Turbine | Pratt & Whitney | FT4-A8 | Mar 1988 | 38 | None | Ultra low sulfur kerosene oil (ULSD) |  | 256 | 0.67 |  | 0.74 |  | 0.67 |  | 20.55 | 1.8 | 2010 | 24 | 5 | 454 | 1.2 | 3.3 | 0.67 | 1.8676 | 4113.7115 | 5575 | Other Oil |  | 2009 | 4 | 5 | 65 | 1.2 | 0.5 | 0.67 | 0.29112 | 4478.6923 | 869 | Other Oil |  | 2008 | 6 | 5 | 112 | 1.2 | 0.8 | 0.67 | 0.45292 | 4043.9286 | 1352 | Other Oil | [6 empty] | 230 |  | 4212.1108 |  | 24 | 454 | 5575 | 1.8676 | 0.67 | 0.67 | 0.027917 | 4 | 65 | 869 | 0.29112 | 0.67 | 0.67 | 0.1675 | 6 | 112 | 1352 | 0.45292 | 0.67 | 0.67 | 0.11167 | 2010 | 24 | 454 | 5575 | 1.8676 | 0.67 | 0.67 | 0.077818 | 3.8909
8300-12 |  | DV11 |  | 24 | 24 | 14 |  | 8300 | 8300-12 | Devon | Devon-11 | DV11 | 40 |  | Combustion Turbine | General Electric | LM6000PA | Jun 1996 | 30 | HPWI | Ultra low sulfur kerosene oil (ULSD) | Natural Gas | 394 | 0.171 |  | 0.171 |  | 0.171 |  | 80.7 | 10.64 | 2010 | 82 | 5 | 2522 | 0.14 | 1.9 | 0.14 | 1.9 | 753.3703 | 26237 | Pipeline Natural Gas | Other Oil | 2009 | 18 | 5 | 496 | 0.15 | 0.4 | 0.15 | 0.4 | 806.4516 | 5266 | Pipeline Natural Gas | Other Oil | 2008 | 16 | 5 | 502 | 0.16 | 0.4 | 0.16 | 0.4 | 796.8127 | 5219 | Pipeline Natural Gas | Other Oil | Water Injection |  |  |  |  | 415 |  | 785.5449 |  | 96 | 2945 | 30042 | 2.3 | 0.15 | 0.15312 | 0.001595 | 19 | 562 | 5896 | 0.5 | 0.15 | 0.16961 | 0.0089267 | 20 | 564 | 5831 | 0.5 | 0.16 | 0.1715 | 0.0085749 | 2010 | 96 | 2945 | 30042 | 2.3 | 0.15 | 0.153 | 0.023958 | 1.1979
8300-13 |  | DV12 |  | 1: 25; 2: 25; 5: 8300; 6: 8300-13; 7: Devon; 8: Devon-12; 9: DV12; 10: 40; 12: Combustion Turbine; 13: General Electric; 14: LM6000PA; 15: Jun 1996; 16: 30; 17: HPWI; 18: Ultra low sulfur kerosene oil (ULSD); 19: Natural Gas; 20: 394; 21: 0.171; 23: 0.171; 25: 0.171; 27: 65.3; 29: 2010; 30: 57; 31: 5; 32: 1771; 33: 0.13; 34: 1.2; 35: 0.13; 36: 1.2; 37: 677.5833; 38: 18265; 39: Pipeline Natural Gas; 40: Other Oil; 41: 2009; 42: 13; 43: 5; 44: 359; 45: 0.12; 46: 0.3; 47: 0.12; 48: 0.3; 49: 835.6546; 50: 4096; 51: Pipeline Natural Gas; 52: Other Oil; 53: 2008; 54: 16; 55: 5; 56: 470; 57: 0.13; 58: 0.4; 59: 0.13; 60: 0.4; 61: 851.0638; 62: 5499; 63: Pipeline Natural Gas; 64: Other Oil; 65: Water Injection; 70: 415; 72: 788.1006; 99: 0
8300-14 |  | DV13 |  | 1: 26; 2: 26; 5: 8300; 6: 8300-14; 7: Devon; 8: Devon-13; 9: DV13; 10: 40; 12: Combustion Turbine; 13: General Electric; 14: LM6000PA; 15: Jun 1996; 16: 30; 17: HPWI; 18: Ultra low sulfur kerosene oil (ULSD); 19: Natural Gas; 20: 394; 21: 0.171; 23: 0.171; 25: 0.171; 27: 94.5; 29: 2010; 30: 85; 31: 5; 32: 2654; 33: 0.15; 34: 2.2; 35: 0.15; 36: 2.2; 37: 828.9375; 38: 27875; 39: Pipeline Natural Gas; 40: Other Oil; 41: 2009; 42: 19; 43: 5; 44: 562; 45: 0.15; 46: 0.5; 47: 0.15; 48: 0.5; 49: 889.6797; 50: 5896; 51: Pipeline Natural Gas; 52: Other Oil; 53: 2008; 54: 17; 55: 5; 56: 496; 57: 0.16; 58: 0.4; 59: 0.16; 60: 0.4; 61: 806.4516; 62: 5267; 63: Pipeline Natural Gas; 64: Other Oil; 65: Water Injection; 70: 415; 72: 841.6896; 99: 0
8300-15 |  | DV14 |  | 1: 27; 2: 27; 5: 8300; 6: 8300-15; 7: Devon; 8: Devon-14; 9: DV14; 10: 40; 12: Combustion Turbine; 13: General Electric; 14: LM6000PA; 15: Jun 1996; 16: 30; 17: HPWI; 18: Ultra low sulfur kerosene oil (ULSD); 19: Natural Gas; 20: 394; 21: 0.171; 23: 0.171; 25: 0.171; 27: 101.4; 29: 2010; 30: 96; 31: 5; 32: 2945; 33: 0.15; 34: 2.3; 35: 0.15; 36: 2.3; 37: 780.9847; 38: 30042; 39: Pipeline Natural Gas; 40: Other Oil; 41: 2009; 42: 16; 43: 5; 44: 443; 45: 0.15; 46: 0.4; 47: 0.15; 48: 0.4; 49: 902.9345; 50: 4653; 51: Pipeline Natural Gas; 52: Other Oil; 53: 2008; 54: 20; 55: 5; 56: 564; 57: 0.16; 58: 0.5; 59: 0.16; 60: 0.5; 61: 886.5248; 62: 5831; 63: Pipeline Natural Gas; 64: Other Oil; 65: Water Injection; 70: 415; 72: 856.8147; 99: 0
8300-16 | NRG | MV10 |  | 1: 28; 2: 28; 3: 15; 4: NRG Energy, Inc; 5: 8300; 6: 8300-16; 7: Montville; 8: Montville-10; 9: MV10; 10: 2.75; 11: 488.5; 12: Diesel Engine; 13: General Motors; 14: EMD 20-645-E4; 15: Jan 1966; 16: 61; 17: None; 18: 0.05% sulfur distillate oil; 20: 29; 21: 3.09; 23: 3.11; 25: 3.09; 27: 235.95; 28: 12; 29: 2010; 35: 3.09; 41: 2009; 47: 3.09; 53: 2008; 59: 3.09; 74: 316.2; 77: 14.1673; 79: 3.09; 80: 0.044805; 81: 111.5; 84: 4.9958; 86: 3.09; 87: 0.044805; 93: 3.09; 96: 316.2; 99: 14.1673; 102: 0.044805; 103: 2.2403; 104: EPA CAIR OS Data not Available - Results are based on NRG data.
8300-17 | NRG | MV11 |  | 1: 29; 2: 29; 5: 8300; 6: 8300-17; 7: Montville; 8: Montville-11; 9: MV11; 10: 2.75; 12: Diesel Engine; 13: General Motors; 14: EMD 20-645-E4; 15: Jan 1966; 16: 61; 17: None; 18: 0.05% sulfur distillate oil; 20: 29; 21: 1.93; 23: 2.96; 25: 1.93; 27: 148.5; 29: 2010; 35: 1.93; 41: 2009; 47: 1.93; 53: 2008; 59: 1.93; 74: 113.5; 77: 3.1763; 79: 1.93; 80: 0.027985; 81: 43.8; 84: 1.2257; 86: 1.93; 87: 0.027985; 93: 1.93; 96: 113.5; 99: 3.1763; 102: 0.027985; 103: 1.3993
8306-01 | NRG | MD2 |  | 30 | 1 | 16 | NRG Energy, Inc | 8306 | 8306-01 | Middletown | Middletown-2 | MD2 | 120 | 953 | Utility Boiler | Riley | Front fired |  |  | None | No. 6 oil | No. 2 oil | 1295 |  |  | 0.18 | as presently controlled | 0.18 |  | 1331.1 | 91.6 | 2010 | 1670 | 5 | 111835 | 0.12 | 94.2 | 0.12 | 94.2 | 842.3123 | 1434563 | Residual Oil | Pipeline Natural Gas | 2009 | 647 | 5 | 40226 | 0.12 | 38.5 | 0.12 | 38.5 | 957.0924 | 528197 | Residual Oil | Pipeline Natural Gas | 2008 | 501 | 5 | 32545 | 0.12 | 33.5 | 0.12 | 33.5 | 1029.344 | 467707 | Residual Oil | Pipeline Natural Gas | Overfire Air |  |  |  | Electrostatic Precipitator | 1295 |  | 942.9162 |  | 1670 | 111835 | 1434563 | 94.2 | 0.12 | 0.13133 | 7.864e-05 | 647 | 40226 | 528197 | 38.5 | 0.12 | 0.14578 | 0.00022532 | 501 | 32545 | 467707 | 33.5 | 0.12 | 0.14325 | 0.00028593 | 2010 | 1670 | 111835 | 1434563 | 94.2 | 0.12 | 0.131 | 0.056407 | 2.8204
8306-02 | NRG | MD3 |  | 31 | 2 | 17 |  | 8306 | 8306-02 | Middletown | Middletown-3 | MD3 | 236 |  | Utility Boiler | Babcock and Wilcox | Cyclone boiler |  |  | None | No. 6 oil | No. 2 oil | 2370 |  |  | 0.27 | as presently controlled | 0.27 |  | 731.05 | 166.49 | 2010 | 1084 | 5 | 141127 | 0.18 | 189.3 | 0.18 | 189.3 | 1341.345 | 1790536 | Residual Oil | Pipeline Natural Gas | 2009 | 293 | 5 | 41047 | 0.23 | 54.4 | 0.23 | 54.4 | 1325.31 | 445004 | Residual Oil | Pipeline Natural Gas | 2008 | 315 | 5 | 32767 | 0.28 | 83.7 | 0.28 | 83.7 | 2554.3992 | 495983 | Residual Oil | Pipeline Natural Gas | Water Injection | Selective Non-catalytic Reduction |  |  | Electrostatic Precipitator | 2370 |  | 1740.3514 |  | 1084 | 141127 | 1790536 | 189.3 | 0.18 | 0.21145 | 0.00019506 | 293 | 41047 | 445004 | 54.4 | 0.23 | 0.24449 | 0.00083444 | 315 | 32767 | 495983 | 83.7 | 0.28 | 0.33751 | 0.0010715 | 2010 | 1084 | 141127 | 1790536 | 189.3 | 0.18 | 0.211 | 0.17463 | 8.7315
8306-03 | NRG | MD4 |  | 32 | 3 | 18 |  | 8306 | 8306-03 | Middletown | Middletown-4 | MD4 | 400 |  | Utility Boiler | Combustion Engineering | Tangential fired |  |  | None | No. 6 oil | No. 2 oil | 4684 |  |  | 0.28 | as presently controlled | 0.28 |  | 243.6 | 78.09 | 2010 | 461 | 5 | 55670 | 0.16 | 80.5 | 0.16 | 80.5 | 1446.0212 | 880454 | Residual Oil |  | 2009 | 74 | 5 | 10926 | 0.16 | 16.8 | 0.16 | 16.8 | 1537.6167 | 173766 | Residual Oil |  | 2008 | 131 | 5 | 15578 | 0.16 | 21 | 0.16 | 21 | 1348.0549 | 224548 | Residual Oil | [6 empty] | 4684 |  | 1443.8976 |  | 461 | 55670 | 880454 | 80.5 | 0.16 | 0.18286 | 0.00039666 | 74 | 10926 | 173766 | 16.8 | 0.16 | 0.19336 | 0.002613 | 131 | 15578 | 224548 | 21 | 0.16 | 0.18704 | 0.0014278 | 2010 | 461 | 55670 | 880454 | 80.5 | 0.16 | 0.183 | 0.17462 | 8.731
8306-04 | NRG | MV5 |  | 33 | 4 | 19 |  | 8306 | 8306-04 | Montville | Montville-5 | MV5 | 81 | 488.5 | Utility Boiler | Combustion Engineering | Tangential fired |  |  | None | No. 6 oil | Nat. Gas | 995 |  |  | 0.23 | as presently controlled | 0.23 |  | 573.9 | 40.56 | 2010 | 932 | 5 | 45896 | 0.09 | 27.4 | 0.09 | 27.4 | 597.0019 | 567960 | Residual Oil | Pipeline Natural Gas | 2009 | 112 | 5 | 6227 | 0.1 | 4.6 | 0.1 | 4.6 | 738.7185 | 75780 | Residual Oil | Pipeline Natural Gas | 2008 | 245 | 5 | 12536 | 0.09 | 8 | 0.09 | 8 | 638.1621 | 148000 | Residual Oil | Pipeline Natural Gas |  |  |  |  | Electrostatic Precipitator | 995 |  | 657.9608 |  | 932 | 45896 | 567960 | 27.4 | 0.09 | 0.096486 | 0.00010353 | 112 | 6227 | 75780 | 4.6 | 0.1 | 0.1214 | 0.001084 | 245 | 12536 | 148000 | 8 | 0.09 | 0.10811 | 0.00044126 | 2010 | 932 | 45896 | 567960 | 27.4 | 0.09 | 0.096 | 0.029399 | 1.47
8306-05 | NRG | MV6 |  | 34 | 5 | 20 |  | 8306 | 8306-05 | Montville | Montville-6 | MV6 | 402 |  | Utility Boiler | Combustion Engineering | Tangential fired |  |  | None | No. 6 oil | No. 2 oil | 4658 |  |  | 0.27 | as presently controlled | 0.27 |  | 231.15 | 60.48 | 2010 | 376 | 5 | 41495 | 0.14 | 44.3 | 0.14 | 44.3 | 1067.5985 | 608716 | Residual Oil |  | 2009 | 146 | 5 | 16484 | 0.16 | 25.4 | 0.16 | 25.4 | 1540.8881 | 253965 | Residual Oil |  | 2008 | 79 | 5 | 14294 | 0.16 | 17.3 | 0.16 | 17.3 | 1210.298 | 178548 | Residual Oil | [6 empty] | 4658 |  | 1272.9282 |  | 376 | 41495 | 608716 | 44.3 | 0.14 | 0.14555 | 0.00038711 | 146 | 16484 | 253965 | 25.4 | 0.16 | 0.20003 | 0.0013701 | 79 | 14294 | 178548 | 17.3 | 0.16 | 0.19379 | 0.002453 | 2010 | 376 | 41495 | 608716 | 44.3 | 0.14 | 0.146 | 0.11782 | 5.891
8306-06 | NRG | NH1 |  | 35 | 6 | 21 |  | 8306 | 8306-06 | Norwalk Harbor Station | Norwalk Harbor-1 | NH1 | 164 | 336 | Utility Boiler | Combustion Engineering | Tangential fired |  |  | None | No. 6 oil | No. 2 oil | 1776 |  |  | 0.21 | as presently controlled | 0.21 |  | 418.45 | 31.48 | 2010 | 707 | 5 | 32380 | 0.13 | 30.6 | 0.13 | 30.6 | 945.0278 | 374772 | Residual Oil |  | 2009 | 219 | 5 | 8286 | 0.1 | 7.6 | 0.1 | 7.6 | 917.2098 | 101788 | Residual Oil |  | 2008 | 829 | 5 | 48368 | 0.14 | 49.5 | 0.14 | 49.5 | 1023.4039 | 624903 | Residual Oil |  | Selective Non-catalytic Reduction |  |  |  | Electrostatic Precipitator | 1776 |  | 961.8805 |  | 707 | 32380 | 374772 | 30.6 | 0.13 | 0.1633 | 0.00023097 | 219 | 8286 | 101788 | 7.6 | 0.1 | 0.14933 | 0.00068187 | 829 | 48368 | 624903 | 49.5 | 0.14 | 0.15842 | 0.0001911 | 2008 | 829 | 48368 | 624903 | 49.5 | 0.14 | 0.158 | 0.05971 | 2.9855
8306-07 | NRG | NH2 |  | 36 | 7 | 22 |  | 8306 | 8306-07 | Norwalk Harbor Station | Norwalk Harbor-2 | NH2 | 172 |  | Utility Boiler | Combustion Engineering | Tangential fired |  |  | None | No. 6 oil | No. 2 oil | 1776 |  |  | 0.21 | as presently controlled | 0.21 |  | 565.35 | 38.86 | 2010 | 711 | 5 | 35972 | 0.13 | 34.3 | 0.13 | 34.3 | 953.5194 | 420206 | Residual Oil |  | 2009 | 184 | 5 | 10175 | 0.13 | 9.1 | 0.13 | 9.1 | 894.3489 | 123688 | Residual Oil |  | 2008 | 1523 | 5 | 75250 | 0.13 | 76.7 | 0.13 | 76.7 | 1019.2691 | 1027131 | Residual Oil |  | Selective Non-catalytic Reduction |  |  |  | Electrostatic Precipitator | 1776 |  | 955.7125 |  | 711 | 35972 | 420206 | 34.3 | 0.13 | 0.16325 | 0.00022961 | 184 | 10175 | 123688 | 9.1 | 0.13 | 0.14714 | 0.0007997 | 1523 | 75250 | 1027131 | 76.7 | 0.13 | 0.14935 | 9.8062e-05 | 2008 | 1523 | 75250 | 1027131 | 76.7 | 0.13 | 0.149 | 0.050361 | 2.5181
8305-01 | PSEG | NHB1 |  | 37 | 10 | 23 | PSEG Power LLC, PSEG Fossil LLC, PSEG Power Connecticut | 8305 | 8305-01 | New Haven Harbor | New Haven Harbor Station (NHHS) - Auxiliary Boiler | NHB1 | Unit is a steam boiler, only | N/A | Utility Boiler | Not Known |  | 1975 | 52 | None | No. 6 oil |  | 143.4 | < 0.4 |  | 0.4 | [5 empty] | 2010 | 849 | 5 | 136402 | 0.13 | 102 | 0.13 | 102 | 747.7896 | 1485780 | Residual Oil | Diesel Oil, Pipeline Natural Gas | 2009 | 205 | 5 | 26780 | 0.14 | 23.9 | 0.14 | 23.9 | 892.4571 | 306139 | Residual Oil | Diesel Oil, Pipeline Natural Gas | 2008 | 227 | 5 | 35856 | 0.15 | 32.2 | 0.15 | 32.2 | 898.0366 | 390698 | Residual Oil | Diesel Oil, Pipeline Natural Gas |  |  |  |  | Electrostatic Precipitator | 4286 |  | 846.0944 |  | 849 | 136402 | 1485780 | 102 | 0.13 | 0.1373 | 0.00016172 | 205 | 26780 | 306139 | 23.9 | 0.14 | 0.15614 | 0.00076165 | 227 | 35856 | 390698 | 32.2 | 0.15 | 0.16483 | 0.00072614 | 2010 | 849 | 136402 | 1485780 | 102 | 0.13 | 0.137 | 0.12014 | 6.0071
8305-02 | PSEG | BHB2 |  | 38 | 8 | 24 |  |  | 8305-02 | Bridgeport Harbor Station | Bridgeport Harbor Station (BHS) Unit No. 2 | BHB2 | 170 | 170 | Utility Boiler | Babcock and Wilcox |  | Aug 1961 | 66 | None | No. 6 oil | No. 2 oil | 1785 | [8 empty] | 2010 | 122 | 5 | 6954 | 0.24 | 11.8 | 0.24 | 11.8 | 1696.8651 | 85201 | Residual Oil | Diesel Oil | 2009 | 64 | 5 | 3168 | 0.2 | 5.4 | 0.2 | 5.4 | 1704.5455 | 39994 | Residual Oil | Diesel Oil | 2008 | 152 | 5 | 6521 | 0.18 | 11.3 | 0.18 | 11.3 | 1732.8631 | 78403 | Residual Oil | Diesel Oil |  |  |  |  | Electrostatic Precipitator | 1785 |  | 1711.4245 |  | 122 | 6954 | 85201 | 11.8 | 0.24 | 0.27699 | 0.0022704 | 64 | 3168 | 39994 | 5.4 | 0.2 | 0.27004 | 0.0042194 | 152 | 6521 | 78403 | 11.3 | 0.18 | 0.28825 | 0.0018964 | 2010 | 122 | 6954 | 85201 | 11.8 | 0.24 | 0.277 | 0.096721 | 4.8361
8305-03 | PSEG | BHB3 |  | 39 | 9 | 25 |  |  | 8305-03 | Bridgeport Harbor Station | Bridgeport Harbor Station (BHS) Unit No. 3 | BHB3 | 410 | 410 | Utility Boiler | Combustion Engineering |  | Aug 1968 | 58 | None | Coal | No. 6 oil | 4100 | [8 empty] | 2010 | 2522 | 5 | 678834 | 0.14 | 500.5 | 0.14 | 500.5 | 737.2937 | 6920835 | Coal | Diesel Oil, Residual Oil | 2009 | 556 | 5 | 129134 | 0.15 | 109.5 | 0.15 | 109.5 | 847.9564 | 1410547 | Coal | Diesel Oil, Residual Oil | 2008 | 3474 | 5 | 1293218 | 0.14 | 916.7 | 0.14 | 916.7 | 708.8519 | 13163750 | Coal | Diesel Oil, Residual Oil | Low NOx Burner Technology w/ Separated OFA |  |  |  | Electrostatic Precipitator | 4100 |  | 764.7006 |  | 2522 | 678834 | 6920835 | 500.5 | 0.14 | 0.14464 | 5.735e-05 | 556 | 129134 | 1410547 | 109.5 | 0.15 | 0.15526 | 0.00027924 | 3474 | 1293218 | 13163750 | 916.7 | 0.14 | 0.13928 | 4.0091e-05 | 2008 | 3474 | 1293218 | 13163750 | 916.7 | 0.14 | 0.139 | 0.26387 | 13.1937
[41 empty] | * Estimated based on NRG Data | [11 empty] | * Estimated based on NRG Data | [11 empty] | * Estimated based on NRG Data | [14 empty] | * Estimated based on NRG Data | [6 empty] | * Estimated based on NRG Data
[32 empty] | 2010 | [11 empty] | 2009 | [11 empty] | 2008
[30 empty] | Totals |  | 2010 |  |  | 1314749 |  |  |  | 1167.1793 |  | 14911044.2609 |  |  | 2009 |  |  | 302208 |  |  |  | 309.057 |  | 3565095.9661 |  |  | 2008 |  |  | 1586253 |  |  |  | 1270.8805 |  | 16991305.1223

## 6(gph)
TA&O EMISSION UNITS NOx GRAPHS
| 1 | Ozone Season NOx Emissions & Emission Rate (3-year Average) for TA&O Turbines | 5 | Ozone Season NOx Emissions & Emissions Rate (3-year Average) for TA&O Boilers
| 2 | Ozone Season 2010, 2009 and 2008 NOx Emissions Rates for TA&O Turbines | 6 | Ozone Season 2010, 2009 and 2008 NOx Emissions Rate for TA&O Boilers
| 3 | Number of Operating Hours During Ozone Season for TA&O Turbines | 7 | Number of Operating Hours During Ozone Season for TA&O Boilers
| 4 | Electric Generation During Ozone Season for TA&O Turbines | 8 | Electric Generation During Ozone Season for TA&O Boilers
| Note: | To print - select the chart and click on print icon
x

## 7(op)
Summary:
[6 empty] | – | Table 4 lists unit owners' proposed NOx Control Technologies for facilities subject to 2010 Trading Agreements and Orders
[6 empty] | – | Also table includes a summary of unit owners' assessment regarding site condition and effectiveness of the proposed NOx control technology
[6 empty] | – | Some records may be not displayed entirely - to view data click on cell or go to Page 4(rd) and select the unit to view all its data.
x
LIST OF NOx CONTROL TECHNOLOGIES / OPTIONS ASSESSSED BY EMMISSION UNIT OWNERS
Table 4
[5 empty] | No. | Lst No. | Owner/Operator | TAO | TA&O ID | Premises/Facility Name | Unit Tag | No identical Units w/ same controls | Site Condition | Site Utilities | Control Option ID | Option No. | NOx Control Technology or Combination of Technologies Proposed | NOx Control Description | Efficiency | Efficiency Remarks | Availability | Stakholder Assessment | Stakeholder Notes
| REFERENCE ID |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19
8298-01 | CDECCA | GT | 8298-01-01 |  | 1: 1; 2: 1; 3: Capitol District Energy Center Cogeneration Associates; 4: 8298; 5: 8298-01; 6: Capitol District Energy Center; 7: GT; 8: 1; 11: 8298-01-01; 12: 1
8302-01 | CRRA | 11A | 8302-01-01 |  | 2 | 2 | Connecticut Resources Recovery Authority | 8302 | 8302-01 | South Meadow Station | 11A | 8 | Very compact, congested if adding new NOx reducing technology. Additional real estate and extensive civil engineering work to re-arrange the site will be needed. Existence of high-voltage power lines limit the available space for new equipment. | Existing fuel tank must be replaced by new smaller tanks. City water is available to supply 200-250 gpm for a new low NOx reduction equipment. | 8302-01-01 | 1 | Selective Catalytic Reduction (SCR)
8302-02 | 0 | 11B | 8302-01-02 |  | 1: 3; 3: 0; 5: 8302-02; 7: 11B; 8: 8; 11: 8302-01-02; 12: 2; 13: HPWI + Ultra Low Sulfur Fuel
8302-03 | 0 | 12A | 8302-01-03 |  | 4 |  | 0 |  | 8302-03 |  | 12A | 8 |  |  | 8302-01-03 | 3 | High Pressure Water Injection (HPWI) | Demineralized water is mixed with the fuel upstream of the combustor and the mixture is injected into the primary combustion zone. The peak flame temperature is lowered and as a result decreases the production of fuel bound NOx. Power output increases by 5%-7% with a decrease in efficiency of approximately 2%. A concern is the incresed emissions of CO and VOC. Additional controls (hence cost) may be needed to limit these emissions, if required. | approx. 60% | would result a 52 ppm NOx | Feasible. A station of water demineralization treatment as well as additional pumps filters and transport accessories are needed. Both are added costs. Rental is not an option due to ISO reliability. | May be considered | Pending the economic and cost factors
8302-04 | 0 | 12B | 8302-01-04 |  | 5 |  | 0 |  | 8302-04 |  | 12B | 8 |  |  | 8302-01-04 | 4 | Dry Low NOx Combustor - DLNC | Addition of a drop-in replacement burners cans kit developed by Wood Group and Pratt & Whitney. Engine re-work was limited to addition of fuel feed - the existing controls were re-used. The solution proved to have a reduced reliability due to early failures of the hot sections of the device. Most of the machines equipped with such kits are being re-converted. | Proved to be efficient | Required NOx reduction could be achieved | No longer available from the OEM due to frequent failures, equipment reliability being an issue. | Rejected | Not reliable; not cost effective
8302-05 | 0 | 13A |  |  | 1: 6; 3: 0; 5: 8302-05; 7: 13A; 8: 8
8302-06 | 0 | 13B |  |  | 1: 7; 3: 0; 5: 8302-06; 7: 13B; 8: 8
8302-07 | 0 | 14A |  |  | 1: 8; 3: 0; 5: 8302-07; 7: 14A; 8: 8
8302-08 | 0 | 14B |  |  | 1: 9; 3: 0; 5: 8302-08; 7: 14B; 8: 8
8303-01 | FirstLight | 10 | 8303-01-01 |  | 1: 10; 2: 3; 3: FirstLight Hydro Generating Company; 4: 8303; 5: 8303-01; 6: Tunnel; 7: 10; 8: 1; 11: 8303-01-01; 12: 1; 13: SCR + HPWI + CO Catalyst + Dual Fuel
|  |  | 8303-01-02 |  | 1: 11; 11: 8303-01-02; 12: 2; 13: SCR + HPWI + CO Catalyst
|  |  | 8303-01-03 |  | 1: 12; 11: 8303-01-03; 12: 3; 13: Selective Catalytic Reduction (SCR)
|  |  | 8303-01-04 |  | 1: 13; 11: 8303-01-04; 12: 4; 13: HPWI with Cookie Cutter Air Deflectors
|  |  | 8303-01-05 |  | 1: 14; 11: 8303-01-05; 12: 5; 13: High Pressure Water Injection (HPWI) - Oil Kerosene K1
|  |  | 8303-01-06 |  | 1: 15; 11: 8303-01-06; 12: 6; 13: Dual Fuel (Natural Gas with Liquid Backup)
|  |  | 8303-01-07 |  | 1: 16; 11: 8303-01-07; 12: 7; 13: LM2500 DLE - new gas fired GE turbine
|  |  | 8303-01-08 |  | 1: 17; 11: 8303-01-08; 12: 8; 13: LM2500 - new oil fired GE turbine
18
8304-01 | NPU | TRBINE | 8304-01-01 |  | 1: 19; 2: 4; 3: Norwich Public Utilities; 4: 8304; 5: 8304-01; 6: Norwich; 7: TRBINE; 8: 1; 11: 8304-01-01; 12: 1; 13: SCR + HPWI + Dual Fuel (Nat Gas - oil backup)
|  |  | 8304-01-02 |  | 1: 20; 11: 8304-01-02; 12: 2; 13: SCR + Water Injection (HPWI) - oil # 2
|  |  | 8304-01-03 |  | 1: 21; 11: 8304-01-03; 12: 3; 13: Selective Catalytic Reduction (SCR)
|  |  | 8304-01-04 |  | 1: 22; 11: 8304-01-04; 12: 4; 13: High Pressure Water Injection (HPWI)
|  |  | 8304-01-05 |  | 1: 23; 11: 8304-01-05; 12: 5; 13: Dual Fuel (Natural Gas with Liquid Backup)
|  |  | 8304-01-06 |  | 1: 24; 11: 8304-01-06; 12: 6; 13: Solar Titan 130 - new dual fuel w/ SoLoNOx
|  |  | 8304-01-07 |  | 1: 25; 11: 8304-01-07; 12: 7; 13: Solar Titan 130 - new oil fired turbine
26
8301-01 | PSEG | BHB4 | 8301-01-01 |  | 1: 27; 2: 5; 3: PSEG Power LLC, PSEG Fossil LLC, PSEG Power Connecticut; 4: 8301; 5: 8301-01; 6: Bridgeport Harbor Station; 7: BHB4; 8: 1; 11: 8301-01-01; 12: 1; 13: Selective Catalytic Reduction (SCR)
|  |  | 8301-01-02 |  | 1: 28; 11: 8301-01-02; 12: 2; 13: High Pressure Water Injection (HPWI)
29
8300-01 | NRG | BR10 | 8300-01-01 |  | 1: 30; 2: 6; 3: NRG Energy, Inc; 4: 8300; 5: 8300-01; 6: Branford; 7: BR10; 8: 1; 11: 8300-01-01; 12: 1; 13: High Pressure Water Injection (HPWI)
8300-02 | NRG | CC10 | 8300-02-01 |  | 1: 31; 2: 7; 5: 8300-02; 6: Cos Cob; 7: CC10; 8: 3; 13: Control option data not provided - No additional NOx controls are feasible, per NRG.; 14: Existing Water Injection; 16: These units Stack Test data (FLER= 0.22 lb/MMBtu) is taken as reference for other facilities as Controlled NOx Rate estimate if HPWI technology is applied.
8300-03 | NRG | CC11 | 8300-03-0 |  | 1: 32; 5: 8300-03; 7: CC11; 8: 3
8300-04 | NRG | CC12 | 8300-04-0 |  | 1: 33; 5: 8300-04; 7: CC12; 8: 3
8300-05 | NRG | CC13 | 8300-05-01 |  | 1: 34; 2: 8; 5: 8300-05; 7: CC13; 8: 2
8300-06 | NRG | CC14 |  |  | 1: 35; 5: 8300-06; 7: CC14; 8: 2
8300-07 | NRG | FD10 | 8300-07-01 |  | 1: 36; 2: 9; 5: 8300-07; 6: Franklin Drive; 7: FD10; 8: 1; 11: 8300-07-01; 12: 1; 13: High Pressure Water Injection (HPWI)
8300-08 | NRG | TT10 | 8300-08-01 |  | 1: 37; 2: 10; 5: 8300-08; 6: Torrington Terminal; 7: TT10; 8: 1; 11: 8300-08-01; 12: 1; 13: High Pressure Water Injection (HPWI)
8300-09 | NRG | MD10 | 8300-09-01 |  | 1: 38; 2: 11; 5: 8300-09; 6: Middletown; 7: MD10; 8: 1; 11: 8300-09-01; 12: 1; 13: High Pressure Water Injection (HPWI)
8300-10 | NRG | NH10 | 8300-10-01 |  | 1: 39; 2: 12; 5: 8300-10; 6: Norwalk Harbor Station; 7: NH10; 8: 1; 11: 8300-10-01; 12: 1; 13: High Pressure Water Injection (HPWI)
8300-11 | NRG | DV10 | 8300-11-01 |  | 1: 40; 2: 13; 5: 8300-11; 6: Devon; 7: DV10; 8: 1; 11: 8300-11-01; 12: 1; 13: Selective Catalytic Reduction (SCR)
|  |  | 8300-11-02 |  | 1: 41; 11: 8300-11-02; 12: 2; 13: High Pressure Water Injection (HPWI)
8300-12 | NRG | DV11 | 8300-12-01 |  | 1: 42; 2: 14; 5: 8300-12; 7: DV11; 8: 4; 11: 8300-12-01; 12: 1; 13: Selective Catalytic Reduction (SCR)
8300-13 | NRG | DV12 |  |  | 1: 43; 5: 8300-13; 7: DV12; 8: 4
8300-14 | NRG | DV13 |  |  | 1: 44; 5: 8300-14; 7: DV13; 8: 4
8300-15 | NRG | DV14 |  |  | 1: 45; 5: 8300-15; 7: DV14; 8: 4
8300-16 | NRG | MV10 | 8300-16-01 |  | 1: 46; 2: 15; 3: NRG Energy, Inc; 5: 8300-16; 6: Montville; 7: MV10; 8: 2; 11: 8300-16-01; 12: 1; 13: Selective Catalytic Reduction (SCR)
8300-17 | NRG | MV11 |  |  | 1: 47; 5: 8300-17; 7: MV11; 8: 2
8306-01 | NRG | MD2 | 8306-01-01 |  | 1: 48; 2: 16; 3: NRG Energy, Inc; 4: 8306; 5: 8306-01; 6: Middletown; 7: MD2; 8: 1; 11: 8306-01-01; 12: 1; 13: Rotating Opposed Fire Air (ROFA)
|  |  | 8306-01-02 |  | 1: 49; 11: 8306-01-02; 12: 2; 13: Selective Catalytic Reduction (SCR) with ID fans
50
8306-02 | NRG | MD3 | 8306-02-01 |  | 1: 51; 2: 17; 5: 8306-02; 7: MD3; 8: 1; 11: 8306-02-01; 12: 1; 13: Separated Overfired Air / High Energy Reagent Technology (SOFA/HERT)
|  |  | 8306-02-02 |  | 1: 52; 11: 8306-02-02; 12: 2; 13: Selective Catalytic Reduction (SCR) with ID fans
53
8306-03 | NRG | MD4 | 8306-03-01 |  | 1: 54; 2: 18; 5: 8306-03; 7: MD4; 8: 1; 11: 8306-03-01; 12: 1; 13: Separated Overfired Air / High Energy Reagent Technology (SOFA/HERT)
|  |  | 8306-03-02 |  | 1: 55; 11: 8306-03-02; 12: 2; 13: Selective Catalytic Reduction (SCR) with ID fans
|  |  | 8306-03-03 |  | 1: 56; 11: 8306-03-03; 12: 3; 13: Selective Catalytic Reduction (SCR)
57
8306-04 | NRG | MV5 | 8306-04-01 |  | 1: 58; 2: 19; 5: 8306-04; 6: Montville; 7: MV5; 8: 1; 11: 8306-04-01; 12: 1; 13: Close Coupled Over Fire Air (CCOFA)
|  |  | 8306-04-02 |  | 1: 59; 11: 8306-04-02; 12: 2; 13: (HERT) High Energy Reagent Technology SNCR
|  |  | 8306-04-03 |  | 1: 60; 11: 8306-04-03; 12: 3; 13: Selective Catalytic Reduction (SCR)
61
8306-05 | NRG | MV6 | 8306-05-01 |  | 1: 62; 2: 20; 5: 8306-05; 7: MV6; 8: 1; 11: 8306-05-01; 12: 1; 13: Separated Overfired Air / High Energy Reagent Technology (SOFA/HERT)
|  |  | 8306-05-02 |  | 1: 63; 11: 8306-05-02; 12: 2; 13: Selective Catalytic Reduction (SCR) with ID fans
|  |  | 8306-05-03 |  | 1: 64; 11: 8306-05-03; 12: 3; 13: Selective Catalytic Reduction (SCR)
65
8306-06 | NRG | NH1 | 8306-06-01 |  | 1: 66; 2: 21; 5: 8306-06; 6: Norwalk Harbor Station; 7: NH1; 8: 1; 11: 8306-06-01; 12: 1; 13: Separated Overfired Air / High Energy Reagent Technology (SOFA/HERT)
|  |  | 8306-06-02 |  | 1: 67; 11: 8306-06-02; 12: 2; 13: Selective Catalytic Reduction (SCR) with ID fans
68
8306-07 | NRG | NH2 | 8306-07-01 |  | 1: 69; 2: 22; 5: 8306-07; 7: NH2; 8: 1; 11: 8306-07-01; 12: 1; 13: Separated Overfired Air / High Energy Reagent Technology (SOFA/HERT)
|  |  | 8306-07-02 |  | 1: 70; 11: 8306-07-02; 12: 2; 13: Selective Catalytic Reduction (SCR) with ID fans
71
8305-01 | PSEG | NHB1 | 8305-01-01 |  | 1: 72; 2: 23; 3: PSEG Power LLC, PSEG Fossil LLC, PSEG Power Connecticut; 4: 8305; 5: 8305-01; 6: New Haven Harbor; 7: NHB1; 8: 1; 11: 8305-01-01; 12: 1; 13: Low NOx Burners (LNB)
|  |  | 8305-01-02 |  | 1: 73; 11: 8305-01-02; 12: 2; 13: Flue Gas Recirculation (FGR)
74
8305-02 | PSEG | BHB2 | 8305-02-01 |  | 1: 75; 2: 24; 5: 8305-02; 6: Bridgeport Harbor Station; 7: BHB2; 8: 1; 11: 8305-02-01; 12: 1; 13: Selective Catalytic Reduction (SCR)
|  |  | 8305-02-02 |  | 1: 76; 11: 8305-02-02; 12: 2; 13: Combination of Control Technologies LNB + OFA + SNCR
|  |  | 8305-02-03 |  | 1: 77; 11: 8305-02-03; 12: 3; 13: Combination of Control Technologies LNB + OFA + FGR
78
8305-03 | PSEG | BHB3 | 8305-03-01 |  | 1: 79; 2: 25; 5: 8305-03; 7: BHB3; 8: 1; 11: 8305-03-01; 12: 1; 13: Work in progress, PSEG asks for more time to develop a solution, due to limited information on the NOx control technologies feasibility on coal boliers
80

## 8(csp)
Summary:
|  | – | Table 5 summarizes owners reports different cost items variation
|  | – | Differences may be due to using various references, different consultants and lack of an uniform guidelines to develop the cost estimates
|  | – | Results below indicate that a leveled cost analysis (adoption of uniform cost items factors) is required in order to perform a comparison and assess TA&O units cost factors.
x
TA&O UNITS OWNERS' COST ANALYSIS REPORTS SPECIFICATIONS
Table 5
| No. | Seq. | Owner / Operator | Site Name | EGU Type | Qty. | Eng. Cosultant | EPA Ref | Cost Analysis Factors
[9 empty] | Total Capital Cost Factors |  |  | Capital Recovery Specifications
[9 empty] | Direct Installation | Indirect Installation | Contingncy | Equip. Life | Interest Rate | Inflation | CRF | Lost Revenue | Unit Operation Time Applied
[9 empty] | % | % | % | yrs | % |  |  |  | hrs
| 1 | No. | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
| 1 | 1 | 2: Capitol District Energy; 3: Capitol District Energy Center; 4: Combustion Turbine; 5: 1; 6: -; % 8: report not provided; yrs 11: report not provided; % 15: -
| 2 | 2 | Connecticut Resources Recovery Authority | South Meadow Station |  | 8 | CCA |  | cummulative (direct+indirect) costs 165% (HPWI) and 199% (SCR) |  | 11% (HPWI) [3] 35% (SCR) | 5 | 6% | 3% per year over 5 yrs |  | - | 48 hrs and 2009 op. time
| 3 | 3 | FirstLight | Tunnel |  | 1 | TRC | 1 | not provided |  |  | 20 | 7% | - |  | included | 50 hrs
| 4 | 4 | Norwich Public Untilities | Norwich |  | 1 | TRC | 1 | 54% | 17% | 15% | 20 | 7% |  | 0.09439 | included | 50
| 5 | 5 | 2: PSEG; 3: Bridgeport Harbor Station; 5: 1; 6: -; % 8: not provided; yrs 11: not provided; % 15: -; hrs 16: not provided
| 6 | 6 | NRG | Branford |  | 1 | NRG | 2 | 45% | 33% | 33% [4] | 15 | 9% | not included | 0.1241 | - | Avg. 2009/2010 actual operation time
| 7 | 7 | 3: Cos Cob; 5: 5
| 8 | 8 | 3: Franklin Drive; 5: 1
| 9 | 9 | 3: Torrington Terminal; 5: 1
| 10 | 10 | 3: Middletown; 5: 1
| 11 | 11 | 3: Norwalk Harbor Station; 5: 1
| 12 | 12 | 3: Devon; 5: 5
| 13 | 1 | NRG | Montville | Diesel Engine | 2 | NRG | 2 | 45% | 33% | 33% [4] | 15 | 9% |  | 0.1241 | - | Avg. 2009/2010
| 14 | 1 | NRG | Middletown | Utility Boiler | 3 | NRG | 2 [1] | 45% | 22% [2] | 15% | 5 | 9% | not included | 0.2571 | - | Avg. 2009/2010 actual operation time
| 15 | 2 | 3: Montville; 5: 2
| 16 | 3 | 3: Norwalk Harbor Station; 5: 2
| 17 | 4 | 2: PSEG; 3: Bridgeport Harbor Station; 5: 2; 6: -; % 8: not provided; yrs 11: not provided; % 15: -; hrs 16: not provided
| 18 | 5 | 3: New Haven Harbor; 5: 1
[16 empty] | Prepared Date: | 2011-06-28
| References |  | % 9: Notes:
| 1 | EPA OAQPS Control Cost Manual, Sixth Edition EPA-452-02-001, January 2002 | % 9: [1]; % 10: Capital and Annual Costs modified (increased) factors (percentages) considered
| 2 | EPA - Alternatve Control Techniques Document - NOx Emissions from Stationary Gas Turbines, January 1993 | % 9: [2]; % 10: Includes 2% preproduction costs
[10 empty] | [3] | CRRA/CCA indicates 10% contingency, however an additional 60% on the top of 10% amount is considered for SCR capital cost assessment
[10 empty] | [4] | NRG Report indicates 20%, but 33% was actually applied

## 9(tcc)
Summary:
| – | Graphical representation below, indicates the Total Capital Cost elements relationship per EPA Air Pollution Control Cost Manual - EPA/452B-02-001, 6th Ed. Jan 2002
| – | Also included the EPA recommended typical values of various cost elements factors (or multipliers)
x
| TOTAL CAPITAL COST ELEMENTS DEFINITION | [18 empty] | 1 | 2 | [12 empty] | Figure 9
TOTAL CAPITAL COST
|  | TOTAL DIRECT COST | [13 empty] | TOTAL INDIRECT COST
|  | PROCUREMENT | [6 empty] | DIRECT INSTALLATION | [6 empty] | INDIRECT INSTALLATION | [6 empty] | CONTINGENCY | [5 empty] | OWNING COST
|  | Purchased Equipment / Procurement Cost | [5 empty] | 3 | Direct Installation Costs | [5 empty] | 8 | Indirect Installation Costs | [5 empty] | 11 | Sale Tax & Contingency Factors |  |  |  |  | 13 | Other Indirect Costs / Miscellaneous | [5 empty] | 15
|  | 1 | Primary Control Device | [5 empty] | 1 | Construction Contracts | [5 empty] | 1 | General Facilities Costs |  |  |  | 5% (A) |  | 1 | Direct / Indirect Cost Sale Tax Estimate (if not else included) |  |  |  |  | ─ | Allowance for Funds during Construction |  |  | E | 0
|  | 2 | Auxiliary Equipment | [6 empty] | ─ | Structural Requirements and Materials | [5 empty] | ─ | Construction Expenses
|  |  | ─ | Primary Control Accessories / Parts | [7 empty] | Foundations, Structures and Supports | [6 empty] | Field Expenses
[5 empty] | Primary Control Device Enclosure | [6 empty] | Structural Steel Materials | [6 empty] | Contractor Fees |  |  |  | 2 | Project Contingency Factors
[5 empty] | Catalyst Box Steel (SCR only) | [6 empty] | Platforms / Misc. Metals | [6 empty] | Construction Incentives |  |  |  |  | ─ | Project Contingency
[5 empty] | Induced Draft Fans | [6 empty] | Stack Foundations | [6 empty] | Construction Services |  |  |  |  | ─ | Economic Conditions
[5 empty] | Ductwork | [6 empty] | Fan Base Steel |  |  |  |  | ─ | Project Management | [5 empty] | ─ | Site Factor
|  |  | ─ | Reagent Storage System | [7 empty] | Duct Supports | [6 empty] | Commissioning |  |  |  |  | ─ | Other Factors (escalation) |  |  |  | ─ | Regulatory Fees and Permits |  |  | F | 0
[5 empty] | Tanks | [6 empty] | Structural Steel Modifications | [6 empty] | Supervisory Personnel | [9 empty] | ─ | Licenses Fees
[5 empty] | Heaters and Accessories |  |  |  |  | ─ | Installation Labor and Materials |  |  |  |  | 2 | Engineering and Home Office |  |  |  | 10% (A) |  | 3 | Construction Contingency |  |  |  |  | ─ | Royalty Allowance
|  |  | ─ | Water Supply and Treatment System | [7 empty] | Control System Field Assembly |  |  |  |  | ─ | Engineering and Testing Contracts | [10 empty] | ─ | Legal Fees
[5 empty] | Demineralizer | [6 empty] | Equipment Insulation & Lagging | [6 empty] | Site Survey | [9 empty] | ─ | Builders Risk Insurance
[5 empty] | Linear Valves and Filters (HPWI ) | [6 empty] | Piping, Valves and Fittings | [6 empty] | Engineering Contracts
[5 empty] | Misc. Pumps | [6 empty] | Insulation and Cladding | [6 empty] | Coordination Engineering
|  |  | ─ | Expansion Joints | [7 empty] | Electrical Accessories | [6 empty] | Modeling | [9 empty] | ─ | Preproduction Costs |  |  | G | 2% (D+E)
|  |  | ─ | Injectors and Injectors Retract | [7 empty] | Painting | [6 empty] | Start-up | [11 empty] | Site Specific Costs
[5 empty] | Retract Panel | [6 empty] | Water System Interconnect | [6 empty] | Stack Inspect / Testing | [11 empty] | Other Testing Contracts
[5 empty] | Distributor Module |  |  |  |  | ─ | Demolition and Clean up | [7 empty] | Initial Testing Fuel | [11 empty] | • | Civil/Structural Testing
|  |  | ─ | Fuel Manifold & Controller | [5 empty] | ─ | Construction Power | [7 empty] | Performance Testing | [11 empty] | • | Noise Testing
|  |  | ─ | Stack Equipment |  |  |  |  | 2 | Modification and Alteration Costs | [8 empty] | Emission Compliance Testing | [11 empty] | Special Modeling (CFD)
|  | 3 | Operation and Control | [6 empty] | ─ | Existing Equipment | [7 empty] | Civil/Structural Testing
|  |  | ─ | System Program Control (PLC, DSC) | [7 empty] | Equipment Modifications | [6 empty] | Noise Testing | [9 empty] | ─ | Inventory Capital |  |  | H | 0
[5 empty] | Control Operation Panel/Display | [6 empty] | Existing Equipment Relocation |  |  |  |  | ─ | Home Office | [11 empty] | (cost for reagent stored at site, i.e. the first fill of the reagent tanks)
[5 empty] | Peripheral Transducers |  |  |  |  | ─ | Piping and Electrical | [7 empty] | Office Personnel
[5 empty] | Control Accessories | [6 empty] | Modification | [6 empty] | Office Fees
|  |  | ─ | Instrumentation | [7 empty] | Relocation | [6 empty] | Temporary Offices
|  |  | ─ | Metering Skid | [5 empty] | ─ | Easement and Building Modification |  |  |  |  | 3 | Process Contingency |  |  |  | 5% (A)
|  | 4 | Electrical Equipment | [5 empty] | 3 | Furnish and Erect Contracts
|  |  | ─ | Power Supply | [5 empty] | ─ | Handling and Erection | [17 empty] | ─ | Initial Accessories Cost |  |  | I | 0
[5 empty] | Power Control Modules (PCM) |  |  |  |  | ─ | Fire Protection System | [18 empty] | • | Catalyst Cost (for SCR)
[5 empty] | Electrical Panels |  |  |  |  | ─ | Stack Priming / Repair
|  |  | ─ | Major Electrical Equipment | [5 empty] | ─ | Acoustical and Vibration Treatment | [17 empty] | ─ | Initial Chemicals Cost
|  | 5 | Other Required Equipment | [6 empty] | ─ | Existing Equipment Repair
|  |  | ─ | Recommended by Manufacturer
|  |  | ─ | Recommended by EPA (see Annex 2) |  |  |  | 4
|  |  | ─ | Other Operation and Control Accessories
|  | Equipment Cost (Total of the above) - EC | [6 empty] | Direct Installation Cost (Total of the above) - DC |  |  |  | DC |  |  | Indirect Installation Cost (Total of the above) - IC
|  | ─ | Sales Tax |  |  |  | 8% EC | 5 | ─ | Sales Tax (usually included in costs above) |  |  |  | 0% | 9 | ─ | Sales Tax (usually included in costs above) |  |  |  | 0%
|  | ─ | Freight | [5 empty] | ─ | Freight (usually included in costs above) | [5 empty] | ─ | Freight (usually included in costs above)
|  | Equipment Procurement Cost = |  |  |  | A1 |  |  | Total Direct Installation Cost = |  |  |  | A2 | 45%(A1) | 10 | Total Indirect Installation Cost |  |  |  | B | 20% (A) | 12 | Total Contingency = |  |  | C | 15% (A+B) | 14 | Total Owning Cost = E + F + G + H + I |  |  |  |  | 2% (D+E)
|  | BUILDING | [26 empty] | Note: |  | D = Total Plant Cost
|  | Buildings Cost (A3) | [5 empty] | 6 | [22 empty] | D = A + B + C as defined below
|  | ─ | Building Construction |  |  | A3 | 0
|  | ─ | Building Alteration
SITE PREPARATION
|  | Site Preparation Cost |  |  |  | A4 | 0 | 7
only required at grass roots installation
|  | TOTAL DIRECT COST = A1 + A2 + A3 + A4= A | [13 empty] | TOTAL INDIRECT INSTALLATION COST = B | [6 empty] | TOTAL CONTINGENCY = C | [5 empty] | TOTAL OWNING COST = E + F + G + H + I
TOTAL PLANT COST = A + B + C = D
TOTAL CAPITAL COST = D + E + F + G + H + I
[12 empty] | ADJUSTED TOTAL CAPITAL COST = TOTAL CAPITAL COST ─ EXISTING EQUIPMENT SALVAGE VALUE + COST OF LOST REVENUES | [14 empty] | 16
NOTES:
| 1 | Total Capital Cost layout is based on the EPA Air Pollution Control Cost Manual - EPA/452B-02-001, 6th Ed. Jan 2002, page 2-6 (pdf file page#20); Tables above include additional cost items found in the stakeholder's cost analysis reports and classified into the appropriate cost elements; | [16 empty] | 9 | Sale Tax and Freight Costs of the direct installation items are in general estimated for each case and included within the cost of the items. The amounts are variable and therefore should not be factored, but rather considered when required and included on a case-by-case basis.
| 2 | The percentage factors recommended by EPA/452/B-02-001 and shown in the above graphical representation of the Total Capital Cost are taken as base factors to perform a leveled cost analysis for the 2010 active Trading Agreements and Orders. | [16 empty] | 10 | Per EPA-453/R-93-007 - ACT document a 45% of the Equipment Procurement Cost (A1) is typical. However there are specific situations (large facilities or facilities within congested sites) where the retrofit cost (Direct Installation Cost) may exceed the Primary Control Procurement Cost, and therefore should be itemized.
| 3 | Equipment Procurement Cost lists the Primary NOx Control Device (or System) plus Auxiliary Equipment and Operation Controls (such as water supply and water treatment, instrumentation and major electrical distribution equipment) necessary for operation of the system or to compensate for loss of performance due to NOx control installation. | [16 empty] | 11 | Indirect Installation includes indirect costs associated with installing, startup and initial performance tests of the equipment, as well as contractor and engineering fees (for construction and engineering firms involved in the project). An additional 5% Process Contingency is recommended by EPA for unexpected costs.
| 4 | The items listed are examples of entries, additional items may be added. For example, Annex 2 published by EPA lists the "Major Equipment for an SCR Application". | [16 empty] | 12 | Per EPA Air Pollution Control Cost Manual - EPA/452/B-02-001, Indirect Costs can be estimated as factors (multipliers) of Total Direct Cost, especially for cost analysis and budget planning purposes. Typical factors listed above for various subgroups are making up an overall Indirect Installation Cost factor of 20% of Total Direct Cost (A).
| 5 | Taxes and Freight Cost covers applicable sales taxes and shipment to the site of the primary control and its auxiliary equipment. 8% figure suggested by EPA is considered appropriate for this cost analysis, since may equal the 6.35% - CT sales tax plus a freight allocation for items that are not free of shipping.
| 6 | In general, installing a NOx control system does not require construction of a new building or major alteration of the existing buildings: | [16 empty] | 13 | Contingencies is a catch-all category that covers unforeseen costs that may arise, possible redesign and modification of equipment, escalation increases in purchase cost, field labor costs and delays encountered in start-up. Sale taxes may be added here if an estimate is not made elsewhere.
|  | ▪ | For small (less that 10MW) and medium size (10-200MW) facilities, buildings alterations and civil work may be included as Construction Contracts or Alteration Costs in section (A2) - Direct Installation Cost, and
[19 empty] | 14 | Contingency elements may be assessed separately, various engineering firms having different approaches. For instance Norwich Public Utility reported a typical 10% of Procurement Cost (A1) in addition to 8% Total Direct and Indirect Installation Costs (A+B). For uniformity EPA's bulk 15% (A+B) was selected for this assessment (EPA/452/B-02-001).
|  | ▪ | For large facilities (such as utility boilers over 200 MW) buildings expenditures would be either listed in section A2 or separately in A3 if the cost is significant.
| 7 | Per EPA, Site Preparation Costs are only required for grass roots installation. Retrofitting an existing facility, depending on the size and site congestion these costs may be significant for large facilities and therefore would be listed separately in section A4; Otherwise items referring to site should be listed within section A2 - Direct Installation Costs (such as site modification, demolition and clean-up and site finishing) or section B - Indirect installation costs (site survey). | [16 empty] | 15 | Other Indirect / Miscellaneous Costs include owning (or owner's) costs. These costs are variable being site specific and also depending of the type of control, facility location, etc.
▪ EPA/452/B-02-001 recommends for Preproduction Costs an overall 2% of Total Direct / Indirect Installation and Contingency (A+B+C).
▪ All other owner costs may be assessed for each facility. However for a direct comparison of various facilities control cost effectiveness a zero dollar value should be assessed.
| 8 | Direct Installation costs include, the labor and materials associated with installing and assembling the primary control and its components. Within this section are listed all construction, mounting, equipment retrofit, relocation and modification work, including cost of bulk parts and accessories (fittings, wiring, pipes, valves, etc.). | [16 empty] | 16 | If the Cost of Loss Revenues is considered for adjusting the Total Capital Cost, then the Existing Equipment Salvage Value should also be included.

## 10(tac)
Summary:
| – | Graphical representation in Figure 10, below, indicates the Total Annual Cost elements interrelationship per EPA Air Pollution Control Cost Manual - EPA/452B-02-001, 6th Ed. Jan 2002
| – | In addition are shown the EPA recommended typical values of various cost elements factors (or multipliers)
| – | Also below are provided in detail two TAC assessesment approach methods (for Water Injection and SCR), based on EPA recommendations. Some cost values (such as actual kWh) are based on TA&O owners reports.
x
TOTAL ANNUAL COST ELEMENTS DEFINITION
[18 empty] | 1 | 2 | [5 empty] | Figure 10
TOTAL ANNUAL COST
[9 empty] | DIRECT COSTS | 5 | [5 empty] | INDIRECT COSTS | [5 empty] | RECOVERY CREDITS
|  | VARIABLE COST | [5 empty] | SEMIVARIABLE COST
|  | 1 | Raw Material / Reagent |  |  | A1 | 3 | 1 | Labor |  |  | B1 |  | 7 |  | 1 | Plant Overhead |  | C1 | 60%(B1+B2) | 10 | 1 | Materials | E1
[9 empty] | ─ | Operating
|  | 2 | Utilities |  |  | A2 | 4 |  | ─ | Supervisory | [5 empty] | 2 | General and Administrative |  | C2 |  | 11 | 2 | Energy | E2
|  |  | ─ | Electricity |  |  |  |  | ─ | Maintenance
|  |  | ─ | Fuel |  | A | [11 empty] | Property Taxes | C | 1% TCC |  |  |  | E
|  |  | ─ | Steam |  |  |  | 2 | Maintenance Materials |  |  | B2 |  | 8 |  |  |  | Insurance |  | 1% TCC
|  |  | ─ | Water |  | A | [11 empty] | Administrative Charges | C | 2% TCC |  |  |  | E
|  |  | ─ | Compressed Air
|  | 3 | Water Treatment / Waste Disposal |  |  | A3 | 5 | 3 | Replacement Parts |  |  | B3 |  | 9 |  | 3 | Capital Recovery |  | C3 | CRF x TCC | 12 |  |  | E
|  | 4 | Performance Loss / Production Loss |  |  | A4 | 6
|  | Total Variable Cost |  |  |  | A |  | Total Semi-Variable Cost |  |  |  | B |  |  |  | Total Indirect Cost |  |  | C |  |  | Total Recovery Credits |  | E |  | 13
NOTES:
| 1 | Total Annual Cost layout, cost items definitions and estimates are based on two EPA documents:
|  | ─ | Alternative Control Techniques Document - NOx Emissions from Stationary Gas Turbines - EPA ACT Document No.: EPA-453/R-93-007, Jan 1993, providing a straightforward method and cost factors for estimating annual cost if Water Injection controls as well as guidelines for SCR applied to combustion turbines.
|  | ─ | EPA Air Pollution Control Cost Manual - Document No.: EPA/452B-02-001, 6th Ed. Jan 2002. This including the above graphical representation on page 2-6 (pdf file page #20), lays out a laborious method for SCR cost assessment.
| 2 | The above graphical representation and EPA's assessment factors of various cost items (detailed below) could be used to perform a leveled cost analysis for 2010 active Trading, Agreements and Order units; The resulted costs ought to be corrected for 2011 using Consumer Price Index (CPI) published by the U.S. Department of Labor, http://www.bls.gov/data/inflation_calculator.htm
| 3 | Variable direct annual cost account for purchase of reagent (A1); Water (for HPWI systems) cost is small , therefore is not considered; However ammonia cost should be included. Proposed cost estimate is per Ref. 2 - EPA-453/R-93-007, page 6-238
| 4 | Utilities also account; EPA proposed values (based on either 1990 or 1998 prices) are provided for equipment operating half-time (4,000 hours) to full year; Since TA&O units are either peaking units (turbines) or demand response generators (utility boilers) the price selected is based on actual costs reported by NRG. Even though the NRG prices are higher than published on the market, the resulted costs are small and may not be taken into account;
| 5 | Water treatment for HPWI is considered negligible - units (combustion turbines_ are generally operating up to only 50 hrs per year. Catalyst disposal cost may be assessed using EPA proposed factor per Ref. 2 - EPA-453/R-93-007, page 6-238
| 6 | Performance loss is calculated for utility boilers per Ref. 2 - EPA-453/R-93-007, page 6-238. Turbines are operating less than 50 hrs, hence performance loss is negligible
| 7 | Labor cost is determined per Ref. 2 - EPA-453/R-93-007, page 6-238. Supervisory costs accounts for 15% of operating hours. Since per Ref. 2 - EPA-453/R-93-007 proposed a Maintenance factor based on a small turbines, the cost factor is assumed to be included in the maintenance materials.
| 8 | Maintenance materials cost and maintenance labor can be determined using factor proposed per EPA/452B-02-001. page 2-45 as a fraction (1.5%) of TCC and adjusted to actual operating hours vs. 4000 hrs per document example.
| 9 | Replacement parts may be significant for SCR's only . It can be assessed per Ref. 1 - EPA/452B-02-001. page 2-50, considering a 1998 cost factor (adjusted with Inflation factor (CPI) and a Capital Recovery Factor (CRF) calculated based on replacement cycle Y = (24,000 / Yearly Operating Hours). The cost is negligible if Y resulted more than 40 years
| 10 | Indirect Overhead cost factor is proposed to 60% labor and maintenance materials without including replacement parts cost, per EPA Ref 1 & 2
| 11 | General and Administrative, property, insurance and other administrative charges) may be calculated together as 4% of TCC. Note the TCC should not include retrofit and other higher costs due to congested sites, EPA estimates did not included these conditions;
| 12 | Capital recovery accounts for more than 70% of the total annual costs and is a fraction of the TCC adjusted by the CRF. For Capital Recovery assessment, TCC should include the retrofitting and other additional costs
| 13 | For TA&O units recovery credits are considered negligible
TOTAL ANNUAL DIRECT COST ASSESSMENT
| HIGH PRESSURE WATER INJECTION | [9 empty] | Reference: | 1 | Alternative Control Techniques Document - EPA ACT Document No.: EPA-453/R-93-007
[12 empty] | 2 | U.S Department of Labor - |  |  |  |  | http://www.bls.gov/data/inflation_calculator.htm
|  | Item Description | [7 empty] | Symbol |  | Unit |  | Equation / or Assumed Value | [6 empty] | Remark
| I. | Data Required
Performance Data
|  |  |  | EGU Heat Input | [5 empty] | HI |  | [MMBtu/yr]
|  |  |  | Operating Hours | [5 empty] | H |  | [hrs]
Cost
|  |  |  | Control Total Capital Cost | [5 empty] | TCC |  | [$/unit]
|  |  |  | Control Equipment Life | [5 empty] | Y |  | [yrs]
|  |  |  | Interest | [5 empty] | n |  | [%]
Assumptions
|  |  |  | Fuel Type | [9 empty] | = | Diesel oil | [5 empty] | Liquid Fuel referenced in EPA-ACT, page 6-213 (#304)
|  |  |  | Lower Heating Value | [5 empty] | LHV |  | [Btu/lb] |  | = | 18330 | [5 empty] | Per Table 6-3, EPA-ACT, page 6-213
|  |  |  | Fuel Density | [5 empty] | ƍ |  | [lb/gal] |  | = | 7.21 | [5 empty] | Per Table 6-3, EPA-ACT, page 6-213
|  |  |  | Fuel consumption | [5 empty] | F |  | [lb/hr] |  | = | (HI x 10^6 /LHV) (Btu/yr x lb/Btu) / H (hr/yr)
|  |  |  | Estimated Water Flow Rate Factor | [5 empty] | WFR |  | [lb water/lb fuel] |  | = | 0.7 | [5 empty] | Per NRG Report (~ 0.66 rounded to 0.70)
|  |  |  | Water Rate | [5 empty] | W |  | [lb/hr] |  | = | (F lb/hr) x WFR (lb water / lb fuel)
|  |  |  | Water (GPM) | [5 empty] | GPM |  | [gal/min] |  | = | W x (7.48 gal/ft³) /62.4 (lb/ft³) x 1/(60 min/hr)
|  |  |  | Electricity | [5 empty] | kW/H |  | [kWh/hr] |  | = | 50 | [5 empty] | Per NRG Report
|  |  |  | Cost of 1 kWh | [7 empty] | [$/MWh] |  | = | 388.16 | [5 empty] | Per NRG (based on Peaking Cost)
|  |  |  | Cost year | [9 empty] | = | 1990 | [5 empty] | Ref. 2 - EPA-453/R-93-007, page 6-238
|  |  |  | Consumer Price Index (1990) | [5 empty] | CFI |  | [$ 2011 / $ 1990] |  | = | 1.73 | [5 empty] | Ref. 3 - Bureau of Statistics CPI Inflation Calculator
Water Cost
[5 empty] | Raw Water Cost | [6 empty] | [$/1,000 gal] |  | = | 0.384 | [5 empty] | Per Table 6-3, EPA-ACT, page 6-213
[5 empty] | Water Treatment Cost | [6 empty] | [$/1,000 gal] |  | = | 1.97 | [5 empty] | Per Table 6-3, EPA-ACT, page 6-213
[5 empty] | Waste Disposal | [6 empty] | [$/1,000 gal] |  | = | 3.82 | [5 empty] | Per Table 6-3, EPA-ACT, page 6-213
|  |  |  | Water (Total) Cost | [5 empty] | WTC |  | [$/1,000 gal] |  | = | 6.174
|  |  |  | Multiplier | [5 empty] | M |  |  |  | = | 1.3 | [5 empty] | Recommended, per Table 6-5, EPA-ACT, page 6-222
Labor Rate
|  |  |  | Operating | [7 empty] | [$ 1990/hr] |  | = | 25.6 | [5 empty] | Per Table 6-3, EPA-ACT, page 6-213
|  |  |  | Supervisory | [7 empty] | [$ 1990/hr] |  | = | 0.15 x 25.60 $1990/hr | [5 empty] | Per Table 6-3, EPA-ACT, page 6-213
|  |  |  | Maintenance | [7 empty] | [$ 1990/hr] |  | = | 31.2 | [5 empty] | Per Table 6-3, EPA-ACT, page 6-213
|  |  |  | Labor Rate (Total) | [5 empty] | LR |  | [$ 1990/hr] |  | = | 60.64
| II. | Total Annual Cost
|  | A. | Direct Variable
|  |  | 1 | Raw Material | [7 empty] | [$/yr] |  | = | None
|  |  | 2 | Electricity | [7 empty] | [$/yr] |  | = | 50 KWh/hr operating time x H x (388.16/1000 $/MWh)
|  |  | 3 | Water (Supply, Treatment Disposal) | [7 empty] | [$/yr] |  | = | (6.174 $/1000 gal) x GPM/1000 x 60 min/hr x (H hr/yr) x 1.73 (CFI) x M
|  | B | Direct Semi-Variable
|  |  | 1 | Labor (Operating, Supervisory, Maintenance) | [7 empty] | [$/yr] |  | = | $60.64 x 1.73 (CFI) x H (hr/yr)
|  |  | 2 | Maintenance Materials | [7 empty] | [$/yr] |  | = | (1.5% TCC) x H/4000 | [5 empty] | Per EPA/452B-02-001. page 2-45 adjusted to actual operating hours vs. 4000 hrs per document example
|  |  | 3 | Replacement Parts | [7 empty] | [$/yr] |  | = | none
|  | C | Indirect Cost
|  |  | 1 | Plant Overhead | [7 empty] | [$/yr] |  | = | 60% (B1 + B2) | [5 empty] | Ref 1, Page 2-34 & Ref 2 Page 6-238
|  |  | 2 | General and Administrative
|  |  |  | ─ | Property Taxes | [6 empty] | [$/yr] |  | = | 1% TCC | [5 empty] | Ref 1, Page 2-34 & Ref 2 Page 6-238
|  |  |  | ─ | Insurance | [6 empty] | [$/yr] |  | = | 1% TCC | [5 empty] | Ref 1, Page 2-34 & Ref 2 Page 6-238
|  |  |  | ─ | Administrative Charges | [6 empty] | [$/yr] |  | = | 2% TCC | [5 empty] | Ref 1, Page 2-34 & Ref 2 Page 6-238
|  |  | 3 | Capital Recovery | [7 empty] | [$/yr] |  | = | CRF x TCC | [5 empty] | Ref 1, Page 2-57 & Ref 2 Page 6-238
|  | E | Recovery Credits | [8 empty] | [$/yr] |  | = | None | [5 empty] | Ref 1, Page 2-57 & Ref 2 Page 6-238 - Not included
|  |  | 1 | Materials | [7 empty] | [$/yr] |  | = | None | [5 empty] | Ref 1, Page 2-57 & Ref 2 Page 6-238 - Not Included
|  |  | 2 | Energy
TOTAL ANNUAL COST ASSESSMENT
| SELECTIVE CATALYTIC REDUCTION - SCR | [9 empty] | References: | 1 | EPA Air Pollution Control Cost Manual - EPA/452B-02-001, 6th Ed. Jan 2002
[12 empty] | 2 | Alternative Control Techniques Document - EPA ACT Document No.: EPA-453/R-93-007
[12 empty] | 3 | U.S Department of Labor - |  |  |  |  | http://www.bls.gov/data/inflation_calculator.htm
|  | Item Description | [7 empty] | Symbol |  | Unit |  | Equation / or Assumed Value | [6 empty] | Remark
| I. | Data Required
Performance Data
|  |  |  | EGU Output, in MW (Nominal or Actual) | [5 empty] | EMW |  | [MW]
|  |  |  | Operating Hours | [5 empty] | H |  | [hrs]
|  |  |  | NOx Removed | [5 empty] | NOx(R) |  | [ton/yr]
Cost
|  |  |  | Control Total Capital Cost | [5 empty] | TCC |  | [$/unit] | [8 empty] | TCC assuming no retrofit cost or (excessive) additional cost due to congested site, cranes etc)
|  |  |  | Control Equipment Life & Interest | [5 empty] | Y, n |  | [yrs], [%]
|  |  |  | Capital Recovery Factor | [5 empty] | CRF |  |  |  | = | Function of (Y, n%) | [5 empty] | From Economic Tables
Assumptions
|  |  |  | Electricity (for boilers) | [5 empty] | kW/H |  | [kWh/hr] |  | = | 200 | [5 empty] | Per NRG Report
|  |  |  | Electricity (for turbines) | [5 empty] | kW/H |  | [kWh/hr] |  | = | 100 | [5 empty] | Per NRG Report
|  |  |  | Cost of 1 kWh | [7 empty] | [$/MWh] |  | = | 212.22 | [5 empty] | Per NRG (based on Fuel Cost)
|  |  |  | Performance Loss | [9 empty] | = | 0.5% | [5 empty] | Ref. 2 - EPA-453/R-93-007, page 6-238
|  |  |  | Production Loss | [9 empty] | = | None | [5 empty] | Ref. 2 - EPA-453/R-93-007, page 6-238
|  |  |  | Catalyst Volume | [5 empty] | V |  | [ft³] |  | = | (EMW) x (6,180 ft³ / 83 MW) | [5 empty] | Ref. 2 - EPA-453/R-93-007, page 6-238
|  |  |  | Catalyst Operating Life | [7 empty] | [hr] |  | = | 24000 | [5 empty] | Ref. 1 - EPA/452B-02-001. page 2-47
|  |  |  | Catalyst Replacement Cycle | [5 empty] | Yc |  | [yrs] |  | = | 24,000 / H
|  |  |  | Annual Interest Rate | [5 empty] | n |  | [%] |  | = | 7% | [5 empty] | Ref. 1 - EPA/452B-02-001. page 2-50
|  |  |  | Capital Recovery Factor | [5 empty] | CRF(c) |  |  |  | = | Function of (Yc, n%) | [5 empty] | From Economic Tables
|  |  |  | Cost year | [9 empty] | = | 1998-12-01 | [5 empty] | Ref. 1 - EPA/452B-02-001. page 2-50
|  |  |  | Consumer Price Index (1998) | [5 empty] | CPI |  | [$/$] |  | = | 1.57 | [5 empty] | Ref. 3 - Bureau of Statistics CPI Inflation Calculator
|  |  |  | Catalyst Cost, Initial | [5 empty] | CCI |  | [$1998/ft³] |  | = | 240 | [5 empty] | Ref. 1 - EPA/452B-02-001. page 2-50
|  |  |  | Catalyst Cost, Replacement | [5 empty] | CCR |  | [$1998/ft³] |  | = | 290 | [5 empty] | Ref. 1 - EPA/452B-02-001. page 2-50
|  |  |  | Cost year | [9 empty] | = | 1990 | [5 empty] | Ref. 2 - EPA-453/R-93-007, page 6-238
|  |  |  | Consumer Price Index (1990) | [5 empty] | CPI |  | [$/$] |  | = | 1.73 | [5 empty] | Ref. 3 - Bureau of Statistics CPI Inflation Calculator
|  |  |  | Catalyst Disposal | [7 empty] | [$1990/ft³] |  | = | 15 | [5 empty] | Ref. 2 - EPA-453/R-93-007, page 6-238
|  |  |  | Anhydrous Ammonia | [5 empty] | N |  | [ton/yr] |  | = | NOx(R) - Molar Ratio NH₃-to-NO₃ = 1.0 | [5 empty] | Ref. 2 - EPA-453/R-93-007, page 6-238
|  |  |  | Ammonia Cost | [7 empty] | [$ 1990/ton] |  | = | 360 | [5 empty] | Ref. 2 - EPA-453/R-93-007, page 6-238
Dilution Steam
|  |  |  | Steam Cost | [10 empty] | 6 | [5 empty] | Ref. 2 - EPA-453/R-93-007, page 6-238
|  |  |  | Dilution Factor (Steam/Ammonia) | [10 empty] | 0.95/0.05 | [5 empty] | Ref. 2 - EPA-453/R-93-007, page 6-238
|  |  |  | Water | [5 empty] | W |  | [ton/yr] |  | = | None ( $ amount too small) | [5 empty] | Ref. 2 - EPA-453/R-93-007, page 6-238
[5 empty] | Water Molecular Weight |  |  |  |  | MW H₂O |  | [lbm/mol] |  | = | 18 lbm/mol | [5 empty] | Table of Elements - Chemistry
[5 empty] | Ammonia Molecular Weight |  |  |  |  | MW NH₃ |  | [lbm/mol] |  | = | 17 lbm/mol | [5 empty] | Table of Elements - Chemistry
Labor Rate
|  |  |  | Operating | [5 empty] | LRO |  | [$ 1990/hr] |  | = | 25.6 | [5 empty] | Per Table 6-3, EPA-ACT, page 6-213
|  |  |  | Supervisory | [5 empty] | LRS |  | [$ 1990/hr] |  | = | 0.15 x 25.60 ($1990/hr) | [5 empty] | Per Table 6-3, EPA-ACT, page 6-213
|  |  |  | Maintenance Labor (included in Maintenance Materials) | [9 empty] | = | 0 | [5 empty] | Per EPA/452B-02-001, 6th Ed. Jan 2002 Page 2-45
|  |  |  | Labor Rate (Total) | [7 empty] | [$ 1990/hr] |  | = | 29.44 | [5 empty] | Per Table 6-3, EPA-ACT, page 6-213
| II. | Total Annual Cost
|  | A. | Direct Variable
|  |  | 1 | Raw Material | [7 empty] | [$/yr] |  | = | None
|  |  |  | ─ | Anhydrous ammonia | [6 empty] | [$/yr] |  | = | (N) x ($360/ton) x 1.73(1990 CPI) | [5 empty] | Ref. 2 - EPA-453/R-93-007, page 6-238
|  |  | 2 | Utilities
|  |  |  | ─ | Electricity | [6 empty] | [$/yr] |  | = | 200 kWh/hr x H x (212.22 /1000 $/Kwh) | [5 empty] | Per NRG Report
|  |  |  | ─ | Blower (if needed) | [6 empty] | [$/yr] |  | = | 10% x (Performance Loss) | [5 empty] | Ref. 2 - EPA-453/R-93-007, page 6-238
|  |  |  | ─ | Dilution steam | [6 empty] | [$/yr] |  | = | (N) x (0.95/0.05) x (MW H₂O/MW NH₃) x ($6/1,000 lb steam) x (2,000 lb/ton) x 1.73(1990CPI) | [5 empty] | Ref. 2 - EPA-453/R-93-007, page 6-238
|  |  | 3 | Water Treatment / Waste Disposal
|  |  |  | ─ | Water Treatment | [8 empty] | = | None | [5 empty] | Water amount too small
|  |  |  | ─ | Catalyst disposal | [6 empty] | [$/yr] |  | = | (V) x ($15/ft³) x CRF(c) X 1.73 (1990CPI) | [5 empty] | Ref. 2 - EPA-453/R-93-007, page 6-238
|  |  | 4 | Performance Loss / Production Loss
|  |  |  | ─ | Performance loss | [6 empty] | [$/yr] |  | = | 0.5% (EMW)x(212.22/1,000kWh)x(1,000kW/MW)x(H) | [5 empty] | Ref. 2 - EPA-453/R-93-007, page 6-238
|  |  |  | ─ | Production loss | [6 empty] | [$/yr] |  | = | None
|  | B | Direct Semi-Variable
|  |  | 1 | Labor (Operating, Supervisory) | [7 empty] | [$/yr] |  | = | $29.44 x 1.73 (CFI) x H (hr/yr) | [5 empty] | Per Table 6-3, EPA-ACT, page 6-213
|  |  | 2 | Maintenance (Labor and Materials) | [7 empty] | [$/yr] |  | = | (1.5% TCC) x H/4000 | [5 empty] | Per EPA/452B-02-001. page 2-45 adjusted to actual operating hours vs. 4000 hrs per document example
|  |  | 3 | Catalyst Replacement | [7 empty] | [$/yr] |  | = | 290($//ft³) x V x CRF x 1.57 (1998 CPI) | [5 empty] | Ref. 1 - EPA/452B-02-001. page 2-50
|  | C | Indirect Cost
|  |  | 1 | Plant Overhead | [7 empty] | [$/yr] |  | = | 60% (B1 + B2) | [5 empty] | Ref 1, Page 2-34 & Ref 2 Page 6-238
|  |  | 2 | General and Administrative
|  |  |  | ─ | Property Taxes | [6 empty] | [$/yr] |  | = | 1% TCC | [5 empty] | Ref 1, Page 2-34 & Ref 2 Page 6-238
|  |  |  | ─ | Insurance | [6 empty] | [$/yr] |  | = | 1% TCC | [5 empty] | Ref 1, Page 2-34 & Ref 2 Page 6-238
|  |  |  | ─ | Administrative Charges | [6 empty] | [$/yr] |  | = | 2% TCC | [5 empty] | Ref 1, Page 2-34 & Ref 2 Page 6-238
|  |  | 3 | Capital Recovery | [7 empty] | [$/yr] |  | = | CRF x TCC | [5 empty] | Ref 1, Page 2-57 & Ref 2 Page 6-238
|  | E | Recovery Credits | [8 empty] | [$/yr] |  | = | None | [5 empty] | Ref 1, Page 2-57 & Ref 2 Page 6-238 - Not included
|  |  | 1 | Materials | [7 empty] | [$/yr] |  | = | None | [5 empty] | Ref 1, Page 2-57 & Ref 2 Page 6-238 - Not Included
|  |  | 2 | Energy

## 11(eff)
Summary:
[7 empty] | – | Table 6 includes Efficiencies of NOx Control Technologies assessed within stakeholders reports and listed in Col. 18-20. These are the values also listed in Section I of Table 1 (General Table) - Page 2 (gnl).
[7 empty] | – | Some fields are blank since owners' reports did not provide NOx rate, yearly amount and efficiencies used.
[7 empty] | – | Achievable efficiencies, published and confirmed by various sources (EPA and NOx Control Technologies Manufacturers) can be selected to override stakeholders data in Col. 25
[7 empty] | – | Newly selected efficiency data can be entered as either percentage efficiency (η%), or as Controlled NOx Rate in (lbm/MMBtu) or (ppmvd)
[7 empty] | – | Depending of the type of data entry, the other efficiency data are immediately calculated and projected in the appropriate cells in Col. 21-23.
[7 empty] | – | These values are farther used for cost analysis using EPA CAIROS records. Results are shown in Section II and III of Table 1 (General Table) - Page 2(gnl)
x
[7 empty] | TA&O UNITS - PROPOSED NOx CONTROL TECHNOLOGIES EFFICENCY ASSESSMENT | [13 empty] | Option No. |  | Data below provided by Stakeholder, is used to assess NOx reduced and Control Effectivess in Section 1 of General Table |  |  | Data below is used to assess NOx reduced and Control Effectivess in Sections 2 and 3 of General Table |  |  |  | Data below can be changed - New selection will overide data in Col(s) 21, 22 & 23 and change the Cost Analysis results in Section II and III of Table 1, page 2(gnl)
[19 empty] | Table 6 | [12 empty] | Table 6
[6 empty] | REGISTRATION & ID | [7 empty] | EMISSION UNIT TAG SPECIFICATIONS |  |  |  | NOx UNCONTROLLED REFERENCE RATE |  | NOx CONTROL TECHNOLOGY |  |  | STAKEHOLDER'S PROPOSED NOx REDUCTION SPECIFICATIONS |  |  | ACHIEVABLE (TARGET) NOx REDUCTION SPECIFICATIONS |  |  |  | NOx Emission Rates / or Control Efficiency - Override Value Selection |  | REMARKS
[6 empty] | No. | Stk No. | Owner/Operator | TA&O | Seq No. | Facility Name | Unit Tag | No identical Units w/ same controls | Nom. Power Capacity | Application Emmision Unit Type | Manufacturer | Model | Stakeholder's Selected Uncontrolled NOx Rate | Stakeholder's Selected Uncontrolled NOx Rate | ID | Option No. | NOx CONTROL SYSTEM(S) | NOx Rate Min Achievable Level |  | Reduction Efficiency | NOx Rate Min Achievable Level |  | Nom.Reduction Efficiency
[23 empty] | Controlled NOx Rate | Controlled NOx Rate |  | Controlled NOx Rate | Controlled NOx Rate
[14 empty] | MW |  |  |  | lbs/MMBtu | ppmvd |  |  |  | lbs/MMBtu | ppmvd | % | lbs/MMBtu | ppmvd | %
REFERENCE ID | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
8298-01 | CDECCA | GT |  | 8298-01 |  | 1: 1; 2: 1; 3: Capitol District Energy Center Cogeneration Associates; 4: 8298; 5: 8298-01; 6: Capitol District Energy Center; 7: GT; 8: 1; MW 10: Combustion Turbine; MW 11: General Electric; MW 12: PG 6531
8302-01 | CRRA | 11A | 8302-01-01 | 8302-01 |  | 2 | 2 | Connecticut Resources Recovery Authority | 8302 | 8302-01 | South Meadow Station | 11A | 8 | 40 | Combustion Turbine | Pratt & Whitney | TP4-2(A9) LF | 0.7305 | 129.3684 | 8302-01-01 | 1 | Selective Catalytic Reduction (SCR) |  |  |  | 0.07305 | 12.9368 | 90% |  | 90 | % | a 90% SCR effciency is considered achievable
8302-02 | 0 | 11B | 8302-01-02 | 8302-01 |  | 1: 3; 3: 0; 5: 8302-02; 7: 11B; ppmvd 15: 8302-01-02; ppmvd 16: 2; ppmvd 17: HPWI + Ultra Low Sulfur Fuel; lbs/MMBtu 21: 0.18263; ppmvd 22: 32.3421; % 23: 75%; % 25: 75 | %
8302-03 | 0 | 12A | 8302-01-03 | 8302-01 |  | 4 |  | 0 |  | 8302-03 |  | 12A |  | 40 | Combustion Turbine | Pratt & Whitney | TP4-2(A9) LF |  |  | 8302-01-03 | 3 | High Pressure Water Injection (HPWI) |  |  |  | 0.2922 | 51.7474 | 60% |  | 60 | %
8302-04 | 0 | 12B |  | 8302-01 |  | 1: 5; 3: 0; 5: 8302-04; 7: 12B; ppmvd 17: Dry Low NOx Combustor - DLNC-Rejected by Stk and hence removed from the list
8302-05 | 0 | 13A |  | 8302-01 |  | 1: 6; 3: 0; 5: 8302-05; 7: 13A; MW 9: 40; MW 10: Combustion Turbine; MW 11: Pratt & Whitney; MW 12: TP4-2(A9) LF
8302-06 | 0 | 13B |  | 8302-01 |  | 1: 7; 3: 0; 5: 8302-06; 7: 13B
8302-07 | 0 | 14A |  | 8302-01 |  | 1: 8; 3: 0; 5: 8302-07; 7: 14A; MW 9: 40; MW 10: Combustion Turbine; MW 11: Pratt & Whitney; MW 12: TP4-2(A9) LF
8302-08 | 0 | 14B |  | 8302-01 |  | 1: 9; 3: 0; 5: 8302-08; 7: 14B
8303-01 | FirstLight | 10 | 8303-01-01 | 8303-01 |  | 10 | 3 | FirstLight Hydro Generating Company | 8303 | 8303-01 | Tunnel | 10 | 1 | 20 | Combustion Turbine | Pratt & Whitney | FT4-8 | 0.736 | 186.7072 | 8303-01-01 | 1 | SCR + HPWI + CO Catalyst + Dual Fuel | 0.01971 | 5 | 97.32% | 0.01971 | 5 | 97.32%
0 |  |  | 8303-01-02 | 8303-01 |  | 1: 11; ppmvd 15: 8303-01-02; ppmvd 16: 2; ppmvd 17: SCR + HPWI + CO Catalyst; lbs/MMBtu 18: 0.03942; ppmvd 19: 10; % 20: 94.64%; lbs/MMBtu 21: 0.03942; ppmvd 22: 10; % 23: 94.64%
0 |  |  | 8303-01-03 | 8303-01 |  | 1: 12; ppmvd 15: 8303-01-03; ppmvd 16: 3; ppmvd 17: Selective Catalytic Reduction (SCR); lbs/MMBtu 18: 0.09855; ppmvd 19: 25; % 20: 86.61%; lbs/MMBtu 21: 0.09855; ppmvd 22: 25; % 23: 86.61%
0 |  |  | 8303-01-04 | 8303-01 |  | 1: 13; ppmvd 15: 8303-01-04; ppmvd 16: 4; ppmvd 17: HPWI with Cookie Cutter Air Deflectors; lbs/MMBtu 18: 0.1971; ppmvd 19: 50; % 20: 73.22%; lbs/MMBtu 21: 0.1971; ppmvd 22: 50; % 23: 73.22%
0 |  |  | 8303-01-05 | 8303-01 |  | 1: 14; ppmvd 15: 8303-01-05; ppmvd 16: 5; ppmvd 17: High Pressure Water Injection (HPWI) - Oil Kerosene K1; lbs/MMBtu 18: 0.29565; ppmvd 19: 75; % 20: 59.83%; lbs/MMBtu 21: 0.29565; ppmvd 22: 75; % 23: 59.83%
0 |  | 0 | 8303-01-06 | 8303-01 |  | 1: 15; ppmvd 15: 8303-01-06; ppmvd 16: 6; ppmvd 17: Dual Fuel (Natural Gas with Liquid Backup); lbs/MMBtu 18: 0.47304; ppmvd 19: 120; % 20: 35.73%; lbs/MMBtu 21: 0.47304; ppmvd 22: 120; % 23: 35.73%
0 |  |  | 8303-01-07 | 8303-01 |  | 1: 16; ppmvd 15: 8303-01-07; ppmvd 16: 7; ppmvd 17: LM2500 DLE - new gas fired GE turbine; lbs/MMBtu 18: 0.09855; ppmvd 19: 25; % 20: 86.61%; lbs/MMBtu 21: 0.09855; ppmvd 22: 25; % 23: 86.61%
0 |  |  | 8303-01-08 | 8303-01 |  | 1: 17; ppmvd 15: 8303-01-08; ppmvd 16: 8; ppmvd 17: LM2500 - new oil fired GE turbine; lbs/MMBtu 18: 0.16556; ppmvd 19: 42; % 20: 77.5%; lbs/MMBtu 21: 0.16556; ppmvd 22: 42; % 23: 77.5%
0 |  |  |  | 8303-01 |  | 1: 18
8304-01 | NPU | TRBINE | 8304-01-01 | 8304-01 |  | 19 | 4 | Norwich Public Utilities | 8304 | 8304-01 | Norwich | TRBINE | 1 | 18.8 | Combustion Turbine | Rolls Royce | Olympus B | 0.553 | 141.31 | 8304-01-01 | 1 | SCR + HPWI + Dual Fuel (Nat Gas - oil backup) | 0.02348 | 6 | 95.75% | 0.02348 | 6 | 95.75%
0 |  |  | 8304-01-02 | 8304-01 |  | 1: 20; ppmvd 15: 8304-01-02; ppmvd 16: 2; ppmvd 17: SCR + Water Injection (HPWI) - oil # 2; lbs/MMBtu 18: 0.03522; ppmvd 19: 9; % 20: 93.63%; lbs/MMBtu 21: 0.03522; ppmvd 22: 9; % 23: 93.63%
0 |  |  | 8304-01-03 | 8304-01 |  | 1: 21; ppmvd 15: 8304-01-03; ppmvd 16: 3; ppmvd 17: Selective Catalytic Reduction (SCR); lbs/MMBtu 18: 0.097835; ppmvd 19: 25; % 20: 82.31%; lbs/MMBtu 21: 0.0553; ppmvd 22: 14.131; % 23: 90%; % 25: 90 | %
0 |  |  | 8304-01-04 | 8304-01 |  | 1: 22; ppmvd 15: 8304-01-04; ppmvd 16: 4; ppmvd 17: High Pressure Water Injection (HPWI); lbs/MMBtu 18: 0.18393; ppmvd 19: 47; % 20: 66.74%; lbs/MMBtu 21: 0.18393; ppmvd 22: 47; % 23: 66.74%
0 |  | 0 | 8304-01-05 | 8304-01 |  | 1: 23; ppmvd 15: 8304-01-05; ppmvd 16: 5; ppmvd 17: Dual Fuel (Natural Gas with Liquid Backup); lbs/MMBtu 18: 0.3522; ppmvd 19: 90; % 20: 36.31%; lbs/MMBtu 21: 0.3522; ppmvd 22: 90; % 23: 36.31%
0 |  |  | 8304-01-06 | 8304-01 |  | 1: 24; ppmvd 15: 8304-01-06; ppmvd 16: 6; ppmvd 17: Solar Titan 130 - new dual fuel w/ SoLoNOx; lbs/MMBtu 18: 0.058701; ppmvd 19: 15; % 20: 89.39%; lbs/MMBtu 21: 0.058701; ppmvd 22: 15; % 23: 89.39%
0 |  | 0 | 8304-01-07 | 8304-01 |  | 1: 25; ppmvd 15: 8304-01-07; ppmvd 16: 7; ppmvd 17: Solar Titan 130 - new oil fired turbine; lbs/MMBtu 18: 0.25437; ppmvd 19: 65; % 20: 54%; lbs/MMBtu 21: 0.25437; ppmvd 22: 65; % 23: 54%
0 |  |  |  | 8304-01 |  | 1: 26
8301-01 | PSEG | BHB4 | 8301-01-01 | 8301-01 |  | 27 | 5 | PSEG Power LLC, PSEG Fossil LLC, PSEG Power Connecticut | 8301 | 8301-01 | Bridgeport Harbor Station | BHB4 | 1 | 22 | Combustion Turbine | Pratt & Whitney | FT-4A-8LI | 0.73 | 186.17 | 8301-01-01 | 1 | Selective Catalytic Reduction (SCR) |  |  |  | 0.073 | 18.617 | 90% |  | 90 | % | a 90% SCR effciency is considered achievable
0 |  |  | 8301-01-02 | 8301-01 |  | 1: 28; ppmvd 15: 8301-01-02; ppmvd 16: 2; ppmvd 17: High Pressure Water Injection (HPWI); lbs/MMBtu 21: 0.292; ppmvd 22: 74.468; % 23: 60%; % 25: 60 | %
0 |  |  |  | 8301-01 |  | 1: 29
8300-01 | NRG | BR10 | 8300-01-01 | 8300-01 |  | 30 | 6 | NRG Energy, Inc | 8300 | 8300-01 | Branford | BR10 | 1 | 20 | Combustion Turbine | Pratt & Whitney | FT4-A8 | 0.8 |  | 8300-01-01 | 1 | High Pressure Water Injection (HPWI) | 0.22 |  | 72.5% | 0.22 |  | 72.5%
8300-02 | NRG | CC10 |  | 8300-02 |  | 1: 31; 5: 8300-02; 6: Cos Cob; 7: CC10; 8: 3; MW 9: 20; MW 10: Combustion Turbine; MW 11: Pratt & Whitney; MW 12: FT4-A9; lbs/MMBtu 13: 0.22 |  | Per NRG - NOx RACT tests performed in 2008 on Cos Cob Units 10 - 14 (equipped w/ HPWI), 2008 indicate a NOx emission rate in the range of 0.171 to 0.194 lb/MMBtu Hence for all NRG units a 0.194 lb/MMBtu rate was selected
8300-03 | NRG | CC11 |  | 8300-02 |  | 1: 32; 5: 8300-03; 7: CC11; 8: 3; lbs/MMBtu 13: 0.22
8300-04 | NRG | CC12 |  | 8300-02 |  | 1: 33; 5: 8300-04; 7: CC12; 8: 3; lbs/MMBtu 13: 0.22
8300-05 | NRG | CC13 |  | 8300-05 |  | 1: 34; 5: 8300-05; 7: CC13; 8: 2; MW 9: 20; MW 10: Combustion Turbine; MW 11: Pratt & Whitney; MW 12: FT4-A9; lbs/MMBtu 13: 0.22
8300-06 | NRG | CC14 |  | 8300-05 |  | 1: 35; 5: 8300-06; 7: CC14; 8: 2; lbs/MMBtu 13: 0.22
8300-07 | NRG | FD10 | 8300-07-01 | 8300-07 |  | 36 |  |  |  | 8300-07 | Franklin Drive | FD10 | 1 | 20 | Combustion Turbine | Pratt & Whitney | FT4-A8 | 0.8 |  | 8300-07-01 | 1 | High Pressure Water Injection (HPWI) | 0.22 |  | 72.5% | 0.22 |  | 72.5% |  |  |  | 0.194 lb/MMBtu is an achievable emission rate confirmed by NRG for facilities with HPWI controls systems (Cos Cob units)
8300-08 | NRG | TT10 | 8300-08-01 | 8300-08 |  | 37 |  |  |  | 8300-08 | Torrington Terminal | TT10 | 1 | 20 | Combustion Turbine | Pratt & Whitney | FT4-A8 | 0.8 |  | 8300-08-01 | 1 | High Pressure Water Injection (HPWI) | 0.22 |  | 72.5% | 0.22 |  | 72.5%
8300-09 | NRG | MD10 | 8300-09-01 | 8300-09 |  | 38 |  |  |  | 8300-09 | Middletown | MD10 | 1 | 20 | Combustion Turbine | Pratt & Whitney | FT4-A8 | 0.67 |  | 8300-09-01 | 1 | High Pressure Water Injection (HPWI) | 0.22 |  | 67.16% | 0.22 |  | 67.16%
8300-10 | NRG | NH10 | 8300-10-01 | 8300-10 |  | 39 |  |  |  | 8300-10 | Norwalk Harbor Station | NH10 | 1 | 17 | Combustion Turbine | Westinghouse | W191 | 0.52 |  | 8300-10-01 | 1 | High Pressure Water Injection (HPWI) | 0.26 |  | 50% | 0.26 |  | 50%
8300-11 | NRG | DV10 | 8300-11-01 | 8300-11 |  | 40 |  |  |  | 8300-11 | Devon | DV10 | 1 | 20 | Combustion Turbine | Pratt & Whitney | FT4-A8 | 0.74 |  | 8300-11-01 | 1 | Selective Catalytic Reduction (SCR) | 0.1 |  | 86.49% | 0.074 |  | 90% |  | 90 | % | a 90% SCR effciency is considered achievable
0 |  |  | 8300-11-02 | 8300-11 |  | 1: 41; ppmvd 15: 8300-11-02; ppmvd 16: 2; ppmvd 17: High Pressure Water Injection (HPWI); lbs/MMBtu 18: 0.22; % 20: 70.27%; lbs/MMBtu 21: 0.22; % 23: 70.27%
8300-12 | NRG | DV11 | 8300-12-01 | 8300-12 |  | 42 |  |  |  | 8300-12 |  | DV11 | 4 | 40 | Combustion Turbine | General Electric | LM6000PA | 0.171 |  | 8300-12-01 | 1 | Selective Catalytic Reduction (SCR) | 0.05 |  | 70.76% | 0.0171 |  | 90% |  | 90 | % | a 90% SCR effciency is considered achievable
8300-13 | NRG | DV12 |  | 8300-12 |  | 1: 43; 5: 8300-13; 7: DV12; 8: 4; MW 9: 40; MW 10: Combustion Turbine; MW 11: General Electric; MW 12: LM6000PA
8300-14 | NRG | DV13 |  | 8300-12 |  | 1: 44; 5: 8300-14; 7: DV13; 8: 4; MW 9: 40; MW 10: Combustion Turbine; MW 11: General Electric; MW 12: LM6000PA
8300-15 | NRG | DV14 |  | 8300-12 |  | 1: 45; 5: 8300-15; 7: DV14; 8: 4; MW 9: 40; MW 10: Combustion Turbine; MW 11: General Electric; MW 12: LM6000PA
8300-16 | NRG | MV10 | 8300-16-01 | 8300-16 |  | 46 | 6 | NRG Energy, Inc |  | 8300-16 | Montville | MV10 | 2 | 2.75 | Diesel Engine | General Motors | EMD 20-645-E4 | 3.11 |  | 8300-16-01 | 1 | Selective Catalytic Reduction (SCR) | 0.933 |  | 70% | 0.311 |  | 90% |  | 90 | % | a 90% SCR effciency is considered achievable
8300-17 | NRG | MV11 |  | 8300-16 |  | 1: 47; 5: 8300-17; 7: MV11; 8: 2; lbs/MMBtu 13: 2.96
8306-01 | NRG | MD2 | 8306-01-01 | 8306-01 |  | 48 | 6 |  | 8306 | 8306-01 | Middletown | MD2 | 1 | 120 | Utility Boiler | Riley | Front fired | 0.18 |  | 8306-01-01 | 1 | Rotating Opposed Fire Air (ROFA) | 0.15 |  | 16.67% | 0.117 |  | 35% |  | 35 | % | same rate as CCOFA
0 |  |  | 8306-01-02 | 8306-01 |  | 1: 49; ppmvd 15: 8306-01-02; ppmvd 16: 2; ppmvd 17: Selective Catalytic Reduction (SCR) with ID fans; lbs/MMBtu 18: 0.1; % 20: 44.44%; lbs/MMBtu 21: 0.018; % 23: 90%; % 25: 90 | % | a 90% SCR effciency is considered achievable
0 |  |  |  | 8306-01 |  | 1: 50
8306-02 | NRG | MD3 | 8306-02-01 | 8306-02 |  | 51 |  |  |  | 8306-02 |  | MD3 | 1 | 236 | Utility Boiler | Babcock and Wilcox | Cyclone boiler | 0.27 |  | 8306-02-01 | 1 | Separated Overfired Air / High Energy Reagent Technology (SOFA/HERT) | 0.15 |  | 44.44% | 0.15 |  | 44.44%
0 |  |  | 8306-02-02 | 8306-02 |  | 1: 52; ppmvd 15: 8306-02-02; ppmvd 16: 2; ppmvd 17: Selective Catalytic Reduction (SCR) with ID fans; lbs/MMBtu 18: 0.1; % 20: 62.96%; lbs/MMBtu 21: 0.027; % 23: 90%; % 25: 90 | % | a 90% SCR effciency is considered achievable
0 |  |  |  | 8306-02 |  | 1: 53
8306-03 | NRG | MD4 | 8306-03-01 | 8306-03 |  | 54 |  |  |  | 8306-03 |  | MD4 | 1 | 400 | Utility Boiler | Combustion Engineering | Tangential fired | 0.28 |  | 8306-03-01 | 1 | Separated Overfired Air / High Energy Reagent Technology (SOFA/HERT) | 0.15 |  | 46.43% | 0.15 |  | 46.43%
0 |  |  | 8306-03-02 | 8306-03 |  | 1: 55; ppmvd 15: 8306-03-02; ppmvd 16: 2; ppmvd 17: Selective Catalytic Reduction (SCR) with ID fans; lbs/MMBtu 18: 0.1; % 20: 64.29%; lbs/MMBtu 21: 0.028; % 23: 90%; % 25: 90 | % | a 90% SCR effciency is considered achievable
0 |  |  | 8306-03-03 | 8306-03 |  | 1: 56; ppmvd 15: 8306-03-03; ppmvd 16: 3; ppmvd 17: Selective Catalytic Reduction (SCR); lbs/MMBtu 18: 0.1; % 20: 64.29%; lbs/MMBtu 21: 0.028; % 23: 90%; % 25: 90 | % | a 90% SCR effciency is considered achievable
0 |  |  |  | 8306-03 |  | 1: 57
8306-04 | NRG | MV5 | 8306-04-01 | 8306-04 |  | 58 |  |  |  | 8306-04 | Montville | MV5 | 1 | 81 | Utility Boiler | Combustion Engineering | Tangential fired | 0.23 |  | 8306-04-01 | 1 | Close Coupled Over Fire Air (CCOFA) | 0.15 |  | 34.78% | 0.15 |  | 34.78%
0 |  |  | 8306-04-02 | 8306-04 |  | 1: 59; ppmvd 15: 8306-04-02; ppmvd 16: 2; ppmvd 17: (HERT) High Energy Reagent Technology SNCR; lbs/MMBtu 18: 0.15; % 20: 34.78%; lbs/MMBtu 21: 0.15; % 23: 34.78%
0 |  |  | 8306-04-03 | 8306-04 |  | 1: 60; ppmvd 15: 8306-04-03; ppmvd 16: 3; ppmvd 17: Selective Catalytic Reduction (SCR); lbs/MMBtu 18: 0.15; % 20: 34.78%; lbs/MMBtu 21: 0.023; % 23: 90%; % 25: 90 | % | a 90% SCR effciency is considered achievable
0 |  |  |  | 8306-04 |  | 1: 61
8306-05 | NRG | MV6 | 8306-05-01 | 8306-05 |  | 62 |  |  |  | 8306-05 |  | MV6 | 1 | 402 | Utility Boiler | Combustion Engineering | Tangential fired | 0.27 |  | 8306-05-01 | 1 | Separated Overfired Air / High Energy Reagent Technology (SOFA/HERT) | 0.15 |  | 44.44% | 0.15 |  | 44.44%
0 |  |  | 8306-05-02 | 8306-05 |  | 1: 63; ppmvd 15: 8306-05-02; ppmvd 16: 2; ppmvd 17: Selective Catalytic Reduction (SCR) with ID fans; lbs/MMBtu 18: 0.1; % 20: 62.96%; lbs/MMBtu 21: 0.027; % 23: 90%; % 25: 90 | % | a 90% SCR effciency is considered achievable
0 |  |  | 8306-05-03 | 8306-05 |  | 1: 64; ppmvd 15: 8306-05-03; ppmvd 16: 3; ppmvd 17: Selective Catalytic Reduction (SCR); lbs/MMBtu 18: 0.1; % 20: 62.96%; lbs/MMBtu 21: 0.027; % 23: 90%; % 25: 90 | % | a 90% SCR effciency is considered achievable
0 |  |  |  | 8306-05 |  | 1: 65
8306-06 | NRG | NH1 | 8306-06-01 | 8306-06 |  | 66 |  |  |  | 8306-06 | Norwalk Harbor Station | NH1 | 1 | 164 | Utility Boiler | Combustion Engineering | Tangential fired | 0.21 |  | 8306-06-01 | 1 | Separated Overfired Air / High Energy Reagent Technology (SOFA/HERT) | 0.15 |  | 28.57% | 0.15 |  | 28.57%
0 |  |  | 8306-06-02 | 8306-06 |  | 1: 67; ppmvd 15: 8306-06-02; ppmvd 16: 2; ppmvd 17: Selective Catalytic Reduction (SCR) with ID fans; lbs/MMBtu 18: 0.1; % 20: 52.38%; lbs/MMBtu 21: 0.021; % 23: 90%; % 25: 90 | % | a 90% SCR effciency is considered achievable
0 |  |  |  | 8306-06 |  | 1: 68
8306-07 | NRG | NH2 | 8306-07-01 | 8306-07 |  | 69 |  |  |  | 8306-07 |  | NH2 | 1 | 172 | Utility Boiler | Combustion Engineering | Tangential fired | 0.21 |  | 8306-07-01 | 1 | Separated Overfired Air / High Energy Reagent Technology (SOFA/HERT) | 0.15 |  | 28.57% | 0.1155 |  | 45% |  | 45 | % | as above for the same control type
0 |  |  | 8306-07-02 | 8306-07 |  | 1: 70; ppmvd 15: 8306-07-02; ppmvd 16: 2; ppmvd 17: Selective Catalytic Reduction (SCR) with ID fans; lbs/MMBtu 18: 0.1; % 20: 52.38%; lbs/MMBtu 21: 0.021; % 23: 90%; % 25: 90 | % | a 90% SCR effciency is considered achievable
0 |  |  |  | 8306-07 |  | 1: 71
8305-01 | PSEG | NHB1 | 8305-01-01 | 8305-01 |  | 72 | 5 | PSEG Power LLC, PSEG Fossil LLC, PSEG Power Connecticut | 8305 | 8305-01 | New Haven Harbor | NHB1 | 1 | Unit is a steam boiler, only | Utility Boiler | Not Known |  | 0.4 |  | 8305-01-01 | 1 | Low NOx Burners (LNB) |  |  |  | 0.28 |  | 30% |  | 30 | %
0 |  |  | 8305-01-02 | 8305-01 |  | 1: 73; ppmvd 15: 8305-01-02; ppmvd 16: 2; ppmvd 17: Flue Gas Recirculation (FGR); lbs/MMBtu 21: 0.28; % 23: 30%; % 25: 30 | %
0 |  |  |  | 8305-01 |  | 1: 74
8305-02 | PSEG | BHB2 | 8305-02-01 | 8305-02 |  | 1: 75; 5: 8305-02; 6: Bridgeport Harbor Station; 7: BHB2; 8: 1; MW 9: 170; MW 10: Utility Boiler; MW 11: Babcock and Wilcox; ppmvd 15: 8305-02-01; ppmvd 16: 1; ppmvd 17: Selective Catalytic Reduction (SCR); % 23: 90%; % 25: 90 | %
0 |  |  | 8305-02-02 | 8305-02 |  | 1: 76; ppmvd 15: 8305-02-02; ppmvd 16: 2; ppmvd 17: Combination of Control Technologies LNB + OFA + SNCR; % 23: 45%; % 25: 45 | %
0 |  | 0 | 8305-02-03 | 8305-02 |  | 1: 77; ppmvd 15: 8305-02-03; ppmvd 16: 3; ppmvd 17: Combination of Control Technologies LNB + OFA + FGR; % 23: 45%; % 25: 45 | %
0 |  |  |  | 8305-02 |  | 1: 78
8305-03 | PSEG | BHB3 | 8305-03-01 | 8305-03 |  | 1: 79; 5: 8305-03; 7: BHB3; 8: 1; MW 9: 410; MW 10: Utility Boiler; MW 11: Combustion Engineering; ppmvd 15: 8305-03-01; ppmvd 16: 1; ppmvd 17: Work in progress, PSEG asks for more time to develop a solution, due to limited information on the NOx control technologies feasibility on coal boliers; % 23: 60%; % 25: 60 | %
0 |  |  |  | 8305-03 |  | 1: 80
Notes:
It is assumed that (in general) NOx Controls maintain the same efficiency within the nominal operational range of Heat Input
Consequently NOx Controlled Rate varies with Heat Input, higher MMBtu means higher lb/MMBtu NOx rates
The above is valid, only if the controls have same (assumed) efficiency at higher Heat Input
Resulted for CAIR OS recorded Heat Input, the Controlled NOx Rate may be different from the above, if control's efficiency is assumed constant

## 12(id)
Summary:
[5 empty] | – | Table below includes entries (input data) from DEEP and stakeholders records, re: Emissions Units ID records and specifications
[5 empty] | – | DEEP Emission Unit Registration Records - Col. 3 - 44
[5 empty] | – | Facility Location, Owner / Operator Contact Information - Col. 45 - 67
[5 empty] | – | NOx Control Cost Analysis Report Reference Information in Col. 68 - 78
[5 empty] | – | Emission Unit General Specification (Model, Manufacturer, Size, Fuel, Nominal Capacity, Age) in Col. 79 - 129
[5 empty] | – | Emission Rates, Stack Tests Data, FLER, AEL, in Col. 130 - 151
[5 empty] | – | Operator Reported Emission Data and Installed Controls, in Col. 130 - 214
x
[5 empty] | EMISSION UNITS ID AND RECORD DATA | [13 empty] | 1 - Single Pack Unit
[17 empty] | Table 7 |  | 2 - Twin Pack Unit
|  |  |  | No. | REFERENCE ID | [17 empty] | DEEP REGISTRATION | [25 empty] | Facility Location | [5 empty] | Contact Information | [16 empty] | Assessment Report | [10 empty] | Application | [5 empty] | Unit Mfg Specifications | [18 empty] | Primary Fuel | [9 empty] | Secondary Fuel | [7 empty] | Alternate Fuel | [7 empty] | Emission Rates | [21 empty] | Report vs. TA&O Document Discrepancies | EPA DATA - Yr around | [11 empty] | OPERATOR REPORTED DATA
[23 empty] | Permit / Registration | [5 empty] | Title IV |  |  | Title V |  |  | Trade Agreement & Order Data | [13 empty] | Premisses No. | Town | Town Code | Client/Seq/Town/Premises | Site | Physical Address | Operator per DEEP | Owner per EPA Report | Client | Sequence | Ownership Starting Date | Owners Group | Operator Name (Company) TAO Respondent | Address | Company Initials | Company's Official | Title | Contact Name | Contact Title | Address | Contact Phone | Fax | email | Report Issued Y/N | Company Issuing Report | Telephone | Fax | Project No. | Prepared By | Date Prepared | Revision No. | Rev Date | Report Objective: | Remarks | Application EPA Designation | Application | SIC Code | Unit Output | App. Notes | App. Remarks | Other in-line unit | EGU Manufacturer | Model | Model Type | Model Description | Arrangement | Power Capacity | Total Site Installed | Nominal BTU Capacity | Generator Name Plate Specifications | Power Output |  |  |  | Unit Age |  |  |  |  | Fuel per Report | Fuel(s) per TA&O and Permit | Primary Fuel | PF Notes | Fuel Rate | units | PFR Notes | Heat Input | PFHINotes | AEL per fuel | Secodary Fuel | SFNotes | SFuel Rate | units | SFRNotes | SFHeat Input | SFHI Notes | AEL per fuel | Alternate Fuel | AFNotes | AFuel Rate | units | AFRNotes | AFHeat Input | AFHI Notes | AEL per fuel | Stack Test Y/N | Heat Input (per TA&O) | Stack Test Rate | Stack Test Rate | Stack Test Notes | FLER Primary Fuel | FLER Primary Fuel | FLER - Gas | FLER - Gas | FLER Notes | AEL | AEL | AEL Notes | Lowest target AEL | Lowest target AEL | Lowest target AEL - Notes | AEL non-ozone season | AEL non-ozone season | AEL non-ozone season - Notes | Date Last ST | Date Next ST | ST Freq |  | 2010 | [5 empty] | 2009 | [5 empty] | Equipment Use and Installed Controls | [6 empty] | 1st Year Data | [13 empty] | 2nd Year Data | [13 empty] | Data Averaging
[5 empty] | ID | Owner/Operator | Owner / Operator Initials | TAO # | Facility Name per EPA CAIROS | Group Name | Group Name (per owner) | Emission Units Group ID | TA&O Unit Registration Tag | Unit ID per Operator | Unit ID per EPA | Facility ID (ORISPL) | Unit Type | No identical Units | Twin Pack/ Single Pack | Seq. No. | TA&O ID | Refer to: | DEEP Registration type | DEEP Registration No. | Date Issued | Expiration Date | DEEP Reg. No. (per Stk Report) | Date Issued (per Stk Report) | TIV Permit No. | Date Issued | Expiration Date | TV Permit No. | Date Issued | Expiration Date | TA&O Objective | RCSA | Date Issued By DEP | Expiration Date | Stakeholder Response Date | Date Received By DEP | Stakeholder Response Revised Date | Date Received Rev By DEP | Prior TAO | Prior TAO Issue Date | Prior TAO | Prior TAO Issue Date | Prior TAO | Prior TAO Issue Date | [50 empty] | Summer Output | POS Notes | Winter Output | POW Notes | Date of Mfg or Installation |  | Estm Date of Installation | Age | Remark | [49 empty] | Year | No Months Reported | Operating Time | Heat Input (MMBtu) | Gross Load | NOx | Year | No Months Reported | Operating Time | Heat Input (MMBtu) | Gross Load | NOx | Equipment Use | Equipment Existing Operating Controls | Equipment Existing NOx Controls | Equipment Existing NOx Controls 02 | SO₂ Controls | PM Controls | Monitoring Controls | Year | Operator Reported Time | Ozone Season Time | Non-Ozone Season Time | Total Os+NOS | OP Hours vs EPA | Heat Input Rate | Heat Input | Heat Input Notes | MWH Generated | MWH Generated Notes | NOx Emission | NOx Emission Note | Operator's Capacity Factor | Year | Operator Reported Time | Ozone Season Time | Non-Ozone Season Time | Total Os+NOS | OP Hours vs EPA | Heat Input Rate | Heat Input | Heat Input Notes | MWH Generated | MWH Generated Notes | NOx Emission | NOx Emission Note | Operator's Capacity Factor | Avg hrs (per Stk) | Avg hrs/2 yrs (clc) | Avg OS hrs/2 yrs | Avg non-OS hrs/2 yrs | Avg Heat Input Rate | Avg Heat Input | Avg Heat Total Combined per group | Avg Heat per unit | MWH Generated | Stack Test NOx Rate | FLER | Selected Uncontrolled NOx | Selected Uncontrolled NOx | NOx - Total per group (per Stk) | NOx Tons/Yr (per unit) | Tons/Yr Calculated
[59 empty] | Yr | [35 empty] | MW | MW | MMBtu/hr |  | MWe |  | MWe |  | month | year |  | yrs | [28 empty] | MMBtu/hr | lbs/MMBtu | ppmvd |  | lb/MMBtu | ppmvd | lb/MMBtu | ppmvd |  | lbs/MMBtu | ppmvd |  | lbs/MMBtu | ppmvd |  | lbs/MMBtu | ppmvd | [7 empty] | hrs | MMBtu | MWh | tons/yr |  |  | hrs | MMBtu | MWh | tons/yr | [8 empty] | hr | hr | hr | hr | hr | MMBtu/yr | MMBtu/yr | [7 empty] | hr | hr | hr | hr | hr | MMBtu/hr | MMBtu/yr |  | MWh |  |  |  |  | hrs | hrs | hrs | hrs | MMBtu/hr | MMBtu/yr | MMBtu | MMBtu | MWh | lbs/MMBtu | lbs/MMBtu | lbs/MMBtu | ppm | tons/yr | tons/yr | tons/yr
REFERENCE ID |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117 | 118 | 119 | 120 | 121 | 122 | 123 | 124 | 125 | 126 | 127 | 128 | 129 | 130 | 131 | 132 | 133 | 134 | 135 | 136 | 137 | 138 | 139 | 140 | 141 | 142 | 143 | 144 | 145 | 146 | 147 | 148 | 149 | 150 | 151 | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181 | 182 | 183 | 184 | 185 | 186 | 187 | 188 | 189 | 190 | 191 | 192 | 193 | 194 | 195 | 196 | 197 | 198 | 199 | 200 | 201 | 202 | 203 | 204 | 205 | 206 | 207 | 208 | 209 | 210 | 211 | 212 | 213 | 214 | 215 | 216
8298-01 | CDECCA | GT |  | 1: 1; 2: 1; 3: Capitol District Energy Center Cogeneration Associates; 4: CDECCA; 5: 8298; 6: Capitol District Energy Center; 7: Capitol District Energy Center; 10: Capital District Energy; 11: GT; 12: GT; 13: 50498; 14: Combustion Turbine; 15: 1; 16: 1; 17: 1; 18: 8298-01; 19: Single turbine; 20: NSR Permit; 21: P-075-0064; 22: 1989-02-01; 23: None; 32: NOx RACT Compliance; 33: 22a-174-22c (CAIR); 34: 2010-04-21; 35: 2013-01-01; 40: 8249; 46: 766; 47: Hartford; 48: 75; 49: - / - / 075 / 0766; 50: Capital District Energy Center - Cogeneration Plant; 51: 490 Capitol Avenue, Hartford, CT 06106; 52: Capitol District Energy Center Cogeneration Assoc.; 53: Capitol District Energy Center Cogeneration Assoc. (Owner) / PurEnergy, LLC (Operator); Yr 56: 2006; Yr 57: Maxim Power (USA) Inc.; Yr 58: Capitol District Energy Center Cogeneration Associates; Yr 59: 490 Capitol Avenue, Hartford, CT 06106; Yr 60: CDECCA; Yr 61: Jamie Urquhart; Yr 62: VP Operations; Yr 69: No; Yr 80: Cogeneration; Yr 81: CHP; Yr 82: 4961; Yr 83: Steam Supply; Yr 86: Duct Burner; Yr 87: General Electric; Yr 88: PG 6531; Yr 89: Cogeneration Turbine; Yr 90: General Electric gas turbine, model PG 6531, with an in-line duct burner; year 102: 1989-02-01; yrs 103: 37.5087; yrs 106: Natural Gas, No.2 oil; yrs 107: Natural Gas; yrs 108: per TA&O; yrs 112: 738.8; yrs 113: per TA&O; yrs 115: No. 2 oil; yrs 116: # 2 Fuel Oil, low Sulfur; yrs 120: 708.2; yrs 121: per TA&O; lbs/MMBtu 141: 0.15; lbs/MMBtu 144: 0.15; ppmvd 154: 2010; ppmvd 155: 12; hrs 156: 308; MMBtu 157: 103236; MWh 158: 11458; tons/yr 159: 5.9; tons/yr 160: 2009; tons/yr 161: 12; hrs 162: 207; MMBtu 163: 69014; MWh 164: 7968; tons/yr 165: 4.1; tons/yr 166: year-round
8302-01 | CRRA | 11A |  | 2 | 2 | Connecticut Resources Recovery Authority | CRRA | 8302 | South Meadow Station | South Meadow Station | South Meadows Jets | GEU-1 | 11A | 11A | 11A | 563 | Combustion Turbine | 8 | 2 | 1 | 8302-01 | Single turbine within a twin pack module | Registration | R-075-0260 |  | None | [5 empty] | 075-0252-TV | 2006-11-20 | 2011-11-20 | NOx RACT Compliance | 22a-174-22c (CAIR) | 2010-04-29 | 2014-05-31 | 2011-01-26 |  | 2011-04-27 | 2011-04-29 | 8116B | [5 empty] | 158 | Hartford | 75 | 5497 / 002 / 075 / 0158 | Reserve - Maxim Roads, Hartford | 20 Reserve Rd Hartford, CT 06114 | Connecticut Resources Recovery Authority | Connecticut Resources Recovery Authority (Owner/Operator) | 5497 | 2 |  |  | Connecticut Resources Recovery Authority | 100 Constitution Plaza, 6th Floor, Hartford, CT 06103 | CRRA | Peter W. Egan | Director of Environmental Affairs and Development | Steven E. Yates | Air Compliance Manager | 100 Constitution Plaza, 6th Floor, Hartford, CT 06103 | (860) 757-7725 |  |  | Yes | Combustion Components Associates, Inc. (CCA) | (203) 268-3139 | (203) 261-7697 | NU-SMEADOW-10-1 | Howard A.S. Brooks and Edmund Schindler | 2011-01-26 | Re-sent modified | 2011-04-29 | Evaluate control technology options to reduce the current NOx level from 130 ppm to between 25 and 50 ppmvd at 15% oxygen |  | Electric Utility | EGU | 4911 | Electric Services | Driven by turbines A and B operating simultaneously |  |  | Pratt & Whitney | TP4-2(A9) LF | TP | Twin pack with two simple cycle turbines (A & B) running simultaneously | Eight (four twin-packs) identical simple cycle gas turbine engine; two turbines per generator operating simultaneously, each turbine has its own stack | 40 | 160 |  | 46,000 kVA, 0.9 PF, 13,800 V, 3 Phase, 60 Hz | 19.3 | at 90ºF | 22.1 | at 90ºF |  | 1970 | 1970-01-01 | 56.5942 | Limited aftermarket suppliers of parts |  | Kerosene A, #2 and other oils | Jet Fuel A (Kerosene K1) | per TitleV Permit & Operator's Report | 1900 | gal/hr | per TitleV Permit | 256 | per TA&O |  | No. 2 oil | per TA&O | 1900 | gal/hr |  | 256 | per TA&O |  | other distillate oil | per TA&O | 1900 | gal/hr |  | 256 | per TA&O |  | CEM | 256 | 0.675 | 132.5 | per TA&O | 0.81 |  |  |  |  | 0.289 | 75 |  | 0.15 | 40 |  |  |  |  | 2009-11-15 | 2014-11-15 | 4.9993 |  | 2010 | 12 | 23 | 3882 | 298 | 1.5 | 2009 | 12 | 22 | 3368 | 264 | 1.4 | Emergency and DR with black start capability, running at full load of 160 MW (40MW/EGU) for 48 hrs, plus any additional time required by ISO-NE | Modbus Modicon TSX Quantum per each EGU - for operation control | None |  |  |  | None | [37 empty] | 0.675 | 0.81 | 0.7305 | 129.3684
8302-02 |  | 11B |  | 1: 3; 5: 8302; 6: South Meadow Station; 8: South Meadows Jets; 9: GEU-1; 10: 11B; 11: 11B; 12: 11B; 13: 563; 14: Combustion Turbine; 15: 8; 16: 2; 17: 2; 18: 8302-02; 19: Single turbine within a twin pack module; 20: Registration; 21: R-075-0261; 23: None; 29: 075-0252-TV; 32: NOx RACT Compliance; 33: 22a-174-22c (CAIR); 34: 2010-04-29; 35: 2014-05-31; 36: 2011-01-26; 38: 2011-04-27; 39: 2011-04-29; 40: 8116B; 46: 158; 47: Hartford; 48: 75; 49: 5497 / 002 / 075 / 0158; 50: Reserve - Maxim Roads, Hartford; 51: 20 Reserve Rd Hartford, CT 06114; 52: Connecticut Resources Recovery Authority; 53: Connecticut Resources Recovery Authority (Owner/Operator); 54: 5497; 55: 2; Yr 58: Connecticut Resources Recovery Authority; Yr 59: 100 Constitution Plaza, 6th Floor, Hartford, CT 06103; Yr 60: CRRA; Yr 61: Peter W. Egan; Yr 62: Director of Environmental Affairs and Development; Yr 63: Steven E. Yates; Yr 64: Air Compliance Manager; Yr 65: 100 Constitution Plaza, 6th Floor, Hartford, CT 06103; Yr 66: (860) 757-7725; Yr 69: Yes; Yr 70: Combustion Components Associates, Inc. (CCA); Yr 71: (203) 268-3139; Yr 72: (203) 261-7697; Yr 73: NU-SMEADOW-10-1; Yr 74: Howard A.S. Brooks and Edmund Schindler; Yr 75: 2011-01-26; Yr 76: Re-sent modified; Yr 77: 2011-04-29; Yr 78: Evaluate control technology options to reduce the current NOx level from 130 ppm to between 25 and 50 ppmvd at 15% oxygen; Yr 80: Electric Utility; Yr 81: EGU; Yr 82: 4911; Yr 83: Electric Services; Yr 84: Driven by turbines B and A operating simultaneously; Yr 87: Pratt & Whitney; Yr 88: TP4-2(A9) LF; Yr 89: TP; Yr 90: Twin pack with two simple cycle turbines (A & B) running simultaneously; Yr 91: Eight (four twin-packs) identical simple cycle gas turbine engine; two turbines per generator operating simultaneously, each turbine has its own stack; MMBtu/hr 95: 46,000 kVA, 0.9 PF, 13,800 V, 3 Phase, 60 Hz; MWe 96: 15.5; MWe 97: at 90ºF; MWe 98: 18.8; MWe 99: at 90ºF; year 101: 1970; year 102: 1970-01-01; yrs 103: 56.5942; yrs 104: limited aftermarket suppliers of parts; yrs 106: Kerosene A, #2 and other oils; yrs 107: Jet Fuel A (Kerosene K1); yrs 108: per TitleV Permit & Operator's Report; yrs 109: 1900; yrs 110: gal/hr; yrs 111: per TitleV Permit; yrs 112: 256; yrs 113: per TA&O; yrs 115: No. 2 oil; yrs 116: per TA&O; yrs 120: 256; yrs 121: per TA&O; yrs 123: other distillate oil; yrs 124: per TA&O; yrs 128: 256; yrs 129: per TA&O; yrs 131: Stack Test; MMBtu/hr 132: 256; lbs/MMBtu 133: 0.71; ppmvd 134: 138.4; ppmvd 135: per TA&O; lb/MMBtu 136: 0.81; lbs/MMBtu 141: 0.289; ppmvd 142: 75; lbs/MMBtu 144: 0.15; ppmvd 150: 2009-11-15; ppmvd 151: 2014-11-15; ppmvd 152: 4.9993; ppmvd 154: 2010; ppmvd 155: 12; hrs 156: 23; MMBtu 157: 3882; MWh 158: 298; tons/yr 159: 1.5; tons/yr 160: 2009; tons/yr 161: 12; hrs 162: 22; MMBtu 163: 3368; MWh 164: 264; tons/yr 165: 1.2; tons/yr 166: Emergency and DR with black start capability, running at full load of 160 MW (40MW/EGU) for 48 hrs, plus any additional time required by ISO-NE; tons/yr 167: Modbus Modicon TSX Quantum per each EGU - for operation control; tons/yr 168: None; tons/yr 172: None; lbs/MMBtu 210: 0.71; lbs/MMBtu 211: 0.81; lbs/MMBtu 212: 0.7305; ppm 213: 129.3684
8302-03 |  | 12A |  | 1: 4; 5: 8302; 6: South Meadow Station; 8: South Meadows Jets; 9: GEU-1; 10: 12A; 11: 12A; 12: 12A; 13: 563; 14: Combustion Turbine; 15: 8; 16: 2; 17: 3; 18: 8302-03; 19: Single turbine within a twin pack module; 20: Registration; 21: R-075-0262; 23: None; 29: 075-0252-TV; 32: NOx RACT Compliance; 33: 22a-174-22c (CAIR); 34: 2010-04-29; 35: 2014-05-31; 36: 2011-01-26; 38: 2011-04-27; 39: 2011-04-29; 40: 8116B; 46: 158; 47: Hartford; 48: 75; 49: 5497 / 002 / 075 / 0158; 50: Reserve - Maxim Roads, Hartford; 51: 20 Reserve Rd Hartford, CT 06114; 52: Connecticut Resources Recovery Authority; 53: Connecticut Resources Recovery Authority (Owner/Operator); 54: 5497; 55: 2; Yr 58: Connecticut Resources Recovery Authority; Yr 59: 100 Constitution Plaza, 6th Floor, Hartford, CT 06103; Yr 60: CRRA; Yr 61: Peter W. Egan; Yr 62: Director of Environmental Affairs and Development; Yr 63: Steven E. Yates; Yr 64: Air Compliance Manager; Yr 65: 100 Constitution Plaza, 6th Floor, Hartford, CT 06103; Yr 66: (860) 757-7725; Yr 69: Yes; Yr 70: Combustion Components Associates, Inc. (CCA); Yr 71: (203) 268-3139; Yr 72: (203) 261-7697; Yr 73: NU-SMEADOW-10-1; Yr 74: Howard A.S. Brooks and Edmund Schindler; Yr 75: 2011-01-26; Yr 76: Re-sent modified; Yr 77: 2011-04-29; Yr 78: Evaluate control technology options to reduce the current NOx level from 130 ppm to between 25 and 50 ppmvd at 15% oxygen; Yr 80: Electric Utility; Yr 81: EGU; Yr 82: 4911; Yr 83: Electric Services; Yr 84: Driven by turbines A and B operating simultaneously; Yr 87: Pratt & Whitney; Yr 88: TP4-2(A9) LF; Yr 89: TP; Yr 90: Twin pack with two simple cycle turbines (A & B) running simultaneously; Yr 91: Eight (four twin-packs) identical simple cycle gas turbine engine; two turbines per generator operating simultaneously, each turbine has its own stack; MW 92: 40; MMBtu/hr 95: 46,000 kVA, 0.9 PF, 13,800 V, 3 Phase, 60 Hz; year 101: 1970; year 102: 1970-01-01; yrs 103: 56.5942; yrs 104: limited aftermarket suppliers of parts; yrs 106: Kerosene A, #2 and other oils; yrs 107: Jet Fuel A (Kerosene K1); yrs 108: per TitleV Permit & Operator's Report; yrs 109: 1900; yrs 110: gal/hr; yrs 111: per TitleV Permit; yrs 112: 256; yrs 113: per TA&O; yrs 115: No. 2 oil; yrs 116: per TA&O; yrs 120: 256; yrs 121: per TA&O; yrs 123: other distillate oil; yrs 124: per TA&O; yrs 128: 256; yrs 129: per TA&O; yrs 131: Stack Test; MMBtu/hr 132: 256; lbs/MMBtu 133: 0.744; ppmvd 134: 124.8; ppmvd 135: per TA&O; lb/MMBtu 136: 0.81; lbs/MMBtu 141: 0.289; ppmvd 142: 75; lbs/MMBtu 144: 0.15; ppmvd 150: 2009-11-14; ppmvd 151: 2014-11-14; ppmvd 152: 4.9993; ppmvd 154: 2010; ppmvd 155: 12; hrs 156: 26; MMBtu 157: 4770; MWh 158: 361; tons/yr 159: 1.9; tons/yr 160: 2009; tons/yr 161: 12; hrs 162: 21; MMBtu 163: 3507; MWh 164: 272; tons/yr 165: 1.4; tons/yr 166: Emergency and DR with black start capability, running at full load of 160 MW (40MW/EGU) for 48 hrs, plus any additional time required by ISO-NE; tons/yr 167: Modbus Modicon TSX Quantum per each EGU - for operation control; tons/yr 168: None; tons/yr 172: None; lbs/MMBtu 210: 0.744; lbs/MMBtu 211: 0.81; lbs/MMBtu 212: 0.7305; ppm 213: 129.3684
8302-04 |  | 12B |  | 1: 5; 5: 8302; 6: South Meadow Station; 8: South Meadows Jets; 9: GEU-1; 10: 12B; 11: 12B; 12: 12B; 13: 563; 14: Combustion Turbine; 15: 8; 16: 2; 17: 4; 18: 8302-04; 19: Single turbine within a twin pack module; 20: Registration; 21: R-075-0263; 23: None; 29: 075-0252-TV; 32: NOx RACT Compliance; 33: 22a-174-22c (CAIR); 34: 2010-04-29; 35: 2014-05-31; 36: 2011-01-26; 38: 2011-04-27; 39: 2011-04-29; 40: 8116B; 46: 158; 47: Hartford; 48: 75; 49: 5497 / 002 / 075 / 0158; 50: Reserve - Maxim Roads, Hartford; 51: 20 Reserve Rd Hartford, CT 06114; 52: Connecticut Resources Recovery Authority; 53: Connecticut Resources Recovery Authority (Owner/Operator); 54: 5497; 55: 2; Yr 58: Connecticut Resources Recovery Authority; Yr 59: 100 Constitution Plaza, 6th Floor, Hartford, CT 06103; Yr 60: CRRA; Yr 61: Peter W. Egan; Yr 62: Director of Environmental Affairs and Development; Yr 63: Steven E. Yates; Yr 64: Air Compliance Manager; Yr 65: 100 Constitution Plaza, 6th Floor, Hartford, CT 06103; Yr 66: (860) 757-7725; Yr 69: Yes; Yr 70: Combustion Components Associates, Inc. (CCA); Yr 71: (203) 268-3139; Yr 72: (203) 261-7697; Yr 73: NU-SMEADOW-10-1; Yr 74: Howard A.S. Brooks and Edmund Schindler; Yr 75: 2011-01-26; Yr 76: Re-sent modified; Yr 77: 2011-04-29; Yr 78: Evaluate control technology options to reduce the current NOx level from 130 ppm to between 25 and 50 ppmvd at 15% oxygen; Yr 80: Electric Utility; Yr 81: EGU; Yr 82: 4911; Yr 83: Electric Services; Yr 84: Driven by turbines B and A operating simultaneously; Yr 87: Pratt & Whitney; Yr 88: TP4-2(A9) LF; Yr 89: TP; Yr 90: Twin pack with two simple cycle turbines (A & B) running simultaneously; Yr 91: Eight (four twin-packs) identical simple cycle gas turbine engine; two turbines per generator operating simultaneously, each turbine has its own stack; MMBtu/hr 95: 46,000 kVA, 0.9 PF, 13,800 V, 3 Phase, 60 Hz; year 101: 1970; year 102: 1970-01-01; yrs 103: 56.5942; yrs 104: limited aftermarket suppliers of parts; yrs 106: Kerosene A, #2 and other oils; yrs 107: Jet Fuel A (Kerosene K1); yrs 108: per TitleV Permit & Operator's Report; yrs 109: 1900; yrs 110: gal/hr; yrs 111: per TitleV Permit; yrs 112: 256; yrs 113: per TA&O; yrs 115: No. 2 oil; yrs 116: per TA&O; yrs 120: 256; yrs 121: per TA&O; yrs 123: other distillate oil; yrs 124: per TA&O; yrs 128: 256; yrs 129: per TA&O; yrs 131: Stack Test; MMBtu/hr 132: 256; lbs/MMBtu 133: 0.706; ppmvd 134: 114.8; ppmvd 135: per TA&O; lb/MMBtu 136: 0.81; lbs/MMBtu 141: 0.289; ppmvd 142: 75; lbs/MMBtu 144: 0.15; ppmvd 150: 2009-11-14; ppmvd 151: 2014-11-14; ppmvd 152: 4.9993; ppmvd 154: 2010; ppmvd 155: 12; hrs 156: 26; MMBtu 157: 4770; MWh 158: 361; tons/yr 159: 1.8; tons/yr 160: 2009; tons/yr 161: 12; hrs 162: 21; MMBtu 163: 3507; MWh 164: 272; tons/yr 165: 1.3; tons/yr 166: Emergency and DR with black start capability, running at full load of 160 MW (40MW/EGU) for 48 hrs, plus any additional time required by ISO-NE; tons/yr 167: Modbus Modicon TSX Quantum per each EGU - for operation control; tons/yr 168: None; tons/yr 172: None; lbs/MMBtu 210: 0.706; lbs/MMBtu 211: 0.81; lbs/MMBtu 212: 0.7305; ppm 213: 129.3684
8302-05 |  | 13A |  | 1: 6; 5: 8302; 6: South Meadow Station; 8: South Meadows Jets; 9: GEU-1; 10: 13A; 11: 13A; 12: 13A; 13: 563; 14: Combustion Turbine; 15: 8; 16: 2; 17: 5; 18: 8302-05; 19: Single turbine within a twin pack module; 20: Registration; 21: R-075-0264; 23: None; 29: 075-0252-TV; 32: NOx RACT Compliance; 33: 22a-174-22c (CAIR); 34: 2010-04-29; 35: 2014-05-31; 36: 2011-01-26; 38: 2011-04-27; 39: 2011-04-29; 40: 8116B; 46: 158; 47: Hartford; 48: 75; 49: 5497 / 002 / 075 / 0158; 50: Reserve - Maxim Roads, Hartford; 51: 20 Reserve Rd Hartford, CT 06114; 52: Connecticut Resources Recovery Authority; 53: Connecticut Resources Recovery Authority (Owner/Operator); 54: 5497; 55: 2; Yr 58: Connecticut Resources Recovery Authority; Yr 59: 100 Constitution Plaza, 6th Floor, Hartford, CT 06103; Yr 60: CRRA; Yr 61: Peter W. Egan; Yr 62: Director of Environmental Affairs and Development; Yr 63: Steven E. Yates; Yr 64: Air Compliance Manager; Yr 65: 100 Constitution Plaza, 6th Floor, Hartford, CT 06103; Yr 66: (860) 757-7725; Yr 69: Yes; Yr 70: Combustion Components Associates, Inc. (CCA); Yr 71: (203) 268-3139; Yr 72: (203) 261-7697; Yr 73: NU-SMEADOW-10-1; Yr 74: Howard A.S. Brooks and Edmund Schindler; Yr 75: 2011-01-26; Yr 76: Re-sent modified; Yr 77: 2011-04-29; Yr 78: Evaluate control technology options to reduce the current NOx level from 130 ppm to between 25 and 50 ppmvd at 15% oxygen; Yr 80: Electric Utility; Yr 81: EGU; Yr 82: 4911; Yr 83: Electric Services; Yr 84: Driven by turbines A and B operating simultaneously; Yr 87: Pratt & Whitney; Yr 88: TP4-2(A9) LF; Yr 89: TP; Yr 90: Twin pack with two simple cycle turbines (A & B) running simultaneously; Yr 91: Eight (four twin-packs) identical simple cycle gas turbine engine; two turbines per generator operating simultaneously, each turbine has its own stack; MW 92: 40; MMBtu/hr 95: 46,000 kVA, 0.9 PF, 13,800 V, 3 Phase, 60 Hz; year 101: 1970; year 102: 1970-01-01; yrs 103: 56.5942; yrs 104: limited aftermarket suppliers of parts; yrs 106: Kerosene A, #2 and other oils; yrs 107: Jet Fuel A (Kerosene K1); yrs 108: per TitleV Permit & Operator's Report; yrs 109: 1900; yrs 110: gal/hr; yrs 111: per TitleV Permit; yrs 112: 256; yrs 113: per TA&O; yrs 115: No. 2 oil; yrs 116: per TA&O; yrs 120: 256; yrs 121: per TA&O; yrs 123: other distillate oil; yrs 124: per TA&O; yrs 128: 256; yrs 129: per TA&O; yrs 131: Stack Test; MMBtu/hr 132: 256; lbs/MMBtu 133: 0.75; ppmvd 134: 132.5; ppmvd 135: per TA&O; lb/MMBtu 136: 0.81; lbs/MMBtu 141: 0.289; ppmvd 142: 75; lbs/MMBtu 144: 0.15; ppmvd 150: 2009-11-08; ppmvd 151: 2014-11-08; ppmvd 152: 4.9993; ppmvd 154: 2010; ppmvd 155: 12; hrs 156: 25; MMBtu 157: 4308; MWh 158: 326; tons/yr 159: 1.8; tons/yr 160: 2009; tons/yr 161: 12; hrs 162: 24; MMBtu 163: 3611; MWh 164: 284; tons/yr 165: 1.5; tons/yr 166: Emergency and DR with black start capability, running at full load of 160 MW (40MW/EGU) for 48 hrs, plus any additional time required by ISO-NE; tons/yr 167: Modbus Modicon TSX Quantum per each EGU - for operation control; tons/yr 168: None; tons/yr 172: None; lbs/MMBtu 210: 0.75; lbs/MMBtu 211: 0.81; lbs/MMBtu 212: 0.7305; ppm 213: 129.3684
8302-06 |  | 13B |  | 1: 7; 5: 8302; 6: South Meadow Station; 8: South Meadows Jets; 9: GEU-1; 10: 13B; 11: 13B; 12: 13B; 13: 563; 14: Combustion Turbine; 15: 8; 16: 2; 17: 6; 18: 8302-06; 19: Single turbine within a twin pack module; 20: Registration; 21: R-075-0265; 23: None; 29: 075-0252-TV; 32: NOx RACT Compliance; 33: 22a-174-22c (CAIR); 34: 2010-04-29; 35: 2014-05-31; 36: 2011-01-26; 38: 2011-04-27; 39: 2011-04-29; 40: 8116B; 46: 158; 47: Hartford; 48: 75; 49: 5497 / 002 / 075 / 0158; 50: Reserve - Maxim Roads, Hartford; 51: 20 Reserve Rd Hartford, CT 06114; 52: Connecticut Resources Recovery Authority; 53: Connecticut Resources Recovery Authority (Owner/Operator); 54: 5497; 55: 2; Yr 58: Connecticut Resources Recovery Authority; Yr 59: 100 Constitution Plaza, 6th Floor, Hartford, CT 06103; Yr 60: CRRA; Yr 61: Peter W. Egan; Yr 62: Director of Environmental Affairs and Development; Yr 63: Steven E. Yates; Yr 64: Air Compliance Manager; Yr 65: 100 Constitution Plaza, 6th Floor, Hartford, CT 06103; Yr 66: (860) 757-7725; Yr 69: Yes; Yr 70: Combustion Components Associates, Inc. (CCA); Yr 71: (203) 268-3139; Yr 72: (203) 261-7697; Yr 73: NU-SMEADOW-10-1; Yr 74: Howard A.S. Brooks and Edmund Schindler; Yr 75: 2011-01-26; Yr 76: Re-sent modified; Yr 77: 2011-04-29; Yr 78: Evaluate control technology options to reduce the current NOx level from 130 ppm to between 25 and 50 ppmvd at 15% oxygen; Yr 80: Electric Utility; Yr 81: EGU; Yr 82: 4911; Yr 83: Electric Services; Yr 84: Driven by turbines B and A operating simultaneously; Yr 87: Pratt & Whitney; Yr 88: TP4-2(A9) LF; Yr 89: TP; Yr 90: Twin pack with two simple cycle turbines (A & B) running simultaneously; Yr 91: Eight (four twin-packs) identical simple cycle gas turbine engine; two turbines per generator operating simultaneously, each turbine has its own stack; MMBtu/hr 95: 46,000 kVA, 0.9 PF, 13,800 V, 3 Phase, 60 Hz; year 101: 1970; year 102: 1970-01-01; yrs 103: 56.5942; yrs 104: limited aftermarket suppliers of parts; yrs 106: Kerosene A, #2 and other oils; yrs 107: Jet Fuel A (Kerosene K1); yrs 108: per TitleV Permit & Operator's Report; yrs 109: 1900; yrs 110: gal/hr; yrs 111: per TitleV Permit; yrs 112: 256; yrs 113: per TA&O; yrs 115: No. 2 oil; yrs 116: per TA&O; yrs 120: 256; yrs 121: per TA&O; yrs 123: other distillate oil; yrs 124: per TA&O; yrs 128: 256; yrs 129: per TA&O; yrs 131: Stack Test; MMBtu/hr 132: 256; lbs/MMBtu 133: 0.733; ppmvd 134: 130.3; ppmvd 135: per TA&O; lb/MMBtu 136: 0.81; lbs/MMBtu 141: 0.289; ppmvd 142: 75; lbs/MMBtu 144: 0.15; ppmvd 150: 2009-11-08; ppmvd 151: 2014-11-08; ppmvd 152: 4.9993; ppmvd 154: 2010; ppmvd 155: 12; hrs 156: 25; MMBtu 157: 4308; MWh 158: 326; tons/yr 159: 1.7; tons/yr 160: 2009; tons/yr 161: 12; hrs 162: 24; MMBtu 163: 3611; MWh 164: 284; tons/yr 165: 1.4; tons/yr 166: Emergency and DR with black start capability, running at full load of 160 MW (40MW/EGU) for 48 hrs, plus any additional time required by ISO-NE; tons/yr 167: Modbus Modicon TSX Quantum per each EGU - for operation control; tons/yr 168: None; tons/yr 172: None; lbs/MMBtu 210: 0.733; lbs/MMBtu 211: 0.81; lbs/MMBtu 212: 0.7305; ppm 213: 129.3684
8302-07 |  | 14A |  | 1: 8; 5: 8302; 6: South Meadow Station; 8: South Meadows Jets; 9: GEU-1; 10: 14A; 11: 14A; 12: 14A; 13: 563; 14: Combustion Turbine; 15: 8; 16: 2; 17: 7; 18: 8302-07; 19: Single turbine within a twin pack module; 20: Registration; 21: R-075-0266; 23: None; 29: 075-0252-TV; 32: NOx RACT Compliance; 33: 22a-174-22c (CAIR); 34: 2010-04-29; 35: 2014-05-31; 36: 2011-01-26; 38: 2011-04-27; 39: 2011-04-29; 40: 8116B; 46: 158; 47: Hartford; 48: 75; 49: 5497 / 002 / 075 / 0158; 50: Reserve - Maxim Roads, Hartford; 51: 20 Reserve Rd Hartford, CT 06114; 52: Connecticut Resources Recovery Authority; 53: Connecticut Resources Recovery Authority (Owner/Operator); 54: 5497; 55: 2; Yr 58: Connecticut Resources Recovery Authority; Yr 59: 100 Constitution Plaza, 6th Floor, Hartford, CT 06103; Yr 60: CRRA; Yr 61: Peter W. Egan; Yr 62: Director of Environmental Affairs and Development; Yr 63: Steven E. Yates; Yr 64: Air Compliance Manager; Yr 65: 100 Constitution Plaza, 6th Floor, Hartford, CT 06103; Yr 66: (860) 757-7725; Yr 69: Yes; Yr 70: Combustion Components Associates, Inc. (CCA); Yr 71: (203) 268-3139; Yr 72: (203) 261-7697; Yr 73: NU-SMEADOW-10-1; Yr 74: Howard A.S. Brooks and Edmund Schindler; Yr 75: 2011-01-26; Yr 76: Re-sent modified; Yr 77: 2011-04-29; Yr 78: Evaluate control technology options to reduce the current NOx level from 130 ppm to between 25 and 50 ppmvd at 15% oxygen; Yr 80: Electric Utility; Yr 81: EGU; Yr 82: 4911; Yr 83: Electric Services; Yr 84: Driven by turbines A and B operating simultaneously; Yr 87: Pratt & Whitney; Yr 88: TP4-2(A9) LF; Yr 89: TP; Yr 90: Twin pack with two simple cycle turbines (A & B) running simultaneously; Yr 91: Eight (four twin-packs) identical simple cycle gas turbine engine; two turbines per generator operating simultaneously, each turbine has its own stack; MW 92: 40; MMBtu/hr 95: 46,000 kVA, 0.9 PF, 13,800 V, 3 Phase, 60 Hz; year 101: 1970; year 102: 1970-01-01; yrs 103: 56.5942; yrs 104: limited aftermarket suppliers of parts; yrs 106: Kerosene A, #2 and other oils; yrs 107: Jet Fuel A (Kerosene K1); yrs 108: per TitleV Permit & Operator's Report; yrs 109: 1900; yrs 110: gal/hr; yrs 111: per TitleV Permit; yrs 112: 256; yrs 113: per TA&O; yrs 115: No. 2 oil; yrs 116: per TA&O; yrs 120: 256; yrs 121: per TA&O; yrs 123: other distillate oil; yrs 124: per TA&O; yrs 128: 256; yrs 129: per TA&O; yrs 131: Stack Test; MMBtu/hr 132: 256; lbs/MMBtu 133: 0.755; ppmvd 134: 124; ppmvd 135: per TA&O; lb/MMBtu 136: 0.81; lbs/MMBtu 141: 0.289; ppmvd 142: 75; lbs/MMBtu 144: 0.15; ppmvd 150: 2009-11-07; ppmvd 151: 2014-11-07; ppmvd 152: 4.9993; ppmvd 154: 2010; ppmvd 155: 12; hrs 156: 24; MMBtu 157: 3909; MWh 158: 296; tons/yr 159: 1.6; tons/yr 160: 2009; tons/yr 161: 12; hrs 162: 19; MMBtu 163: 3094; MWh 164: 239; tons/yr 165: 1.3; tons/yr 166: Emergency and DR with black start capability, running at full load of 160 MW (40MW/EGU) for 48 hrs, plus any additional time required by ISO-NE; tons/yr 167: Modbus Modicon TSX Quantum per each EGU - for operation control; tons/yr 168: None; tons/yr 172: None; lbs/MMBtu 210: 0.755; lbs/MMBtu 211: 0.81; lbs/MMBtu 212: 0.7305; ppm 213: 129.3684
8302-08 |  | 14B |  | 1: 9; 5: 8302; 6: South Meadow Station; 8: South Meadows Jets; 9: GEU-1; 10: 14B; 11: 14B; 12: 14B; 13: 563; 14: Combustion Turbine; 15: 8; 16: 2; 17: 8; 18: 8302-08; 19: Single turbine within a twin pack module; 20: Registration; 21: R-075-0267; 23: None; 29: 075-0252-TV; 32: NOx RACT Compliance; 33: 22a-174-22c (CAIR); 34: 2010-04-29; 35: 2014-05-31; 36: 2011-01-26; 38: 2011-04-27; 39: 2011-04-29; 40: 8116B; 46: 158; 47: Hartford; 48: 75; 49: 5497 / 002 / 075 / 0158; 50: Reserve - Maxim Roads, Hartford; 51: 20 Reserve Rd Hartford, CT 06114; 52: Connecticut Resources Recovery Authority; 53: Connecticut Resources Recovery Authority (Owner/Operator); 54: 5497; 55: 2; Yr 58: Connecticut Resources Recovery Authority; Yr 59: 100 Constitution Plaza, 6th Floor, Hartford, CT 06103; Yr 60: CRRA; Yr 61: Peter W. Egan; Yr 62: Director of Environmental Affairs and Development; Yr 63: Steven E. Yates; Yr 64: Air Compliance Manager; Yr 65: 100 Constitution Plaza, 6th Floor, Hartford, CT 06103; Yr 66: (860) 757-7725; Yr 69: Yes; Yr 70: Combustion Components Associates, Inc. (CCA); Yr 71: (203) 268-3139; Yr 72: (203) 261-7697; Yr 73: NU-SMEADOW-10-1; Yr 74: Howard A.S. Brooks and Edmund Schindler; Yr 75: 2011-01-26; Yr 76: Re-sent modified; Yr 77: 2011-04-29; Yr 78: Evaluate control technology options to reduce the current NOx level from 130 ppm to between 25 and 50 ppmvd at 15% oxygen; Yr 80: Electric Utility; Yr 81: EGU; Yr 82: 4911; Yr 83: Electric Services; Yr 84: Driven by turbines B and 0 operating simultaneously; Yr 87: Pratt & Whitney; Yr 88: TP4-2(A9) LF; Yr 89: TP; Yr 90: Twin pack with two simple cycle turbines (A & B) running simultaneously; Yr 91: Eight (four twin-packs) identical simple cycle gas turbine engine; two turbines per generator operating simultaneously, each turbine has its own stack; MMBtu/hr 95: 46,000 kVA, 0.9 PF, 13,800 V, 3 Phase, 60 Hz; year 101: 1970; year 102: 1970-01-01; yrs 103: 56.5942; yrs 104: limited aftermarket suppliers of parts; yrs 106: Kerosene A, #2 and other oils; yrs 107: Jet Fuel A (Kerosene K1); yrs 108: per TitleV Permit & Operator's Report; yrs 109: 1900; yrs 110: gal/hr; yrs 111: per TitleV Permit; yrs 112: 256; yrs 113: per TA&O; yrs 115: No. 2 oil; yrs 116: per TA&O; yrs 120: 256; yrs 121: per TA&O; yrs 123: other distillate oil; yrs 124: per TA&O; yrs 128: 256; yrs 129: per TA&O; yrs 131: Stack Test; MMBtu/hr 132: 256; lbs/MMBtu 133: 0.771; ppmvd 134: 136.1; ppmvd 135: per TA&O; lb/MMBtu 136: 0.81; lbs/MMBtu 141: 0.289; ppmvd 142: 75; lbs/MMBtu 144: 0.15; ppmvd 150: 2009-11-07; ppmvd 151: 2014-11-07; ppmvd 152: 4.9993; ppmvd 154: 2010; ppmvd 155: 12; hrs 156: 24; MMBtu 157: 3909; MWh 158: 296; tons/yr 159: 1.7; tons/yr 160: 2009; tons/yr 161: 12; hrs 162: 19; MMBtu 163: 3094; MWh 164: 239; tons/yr 165: 1.2; tons/yr 166: Emergency and DR with black start capability, running at full load of 160 MW (40MW/EGU) for 48 hrs, plus any additional time required by ISO-NE; tons/yr 167: Modbus Modicon TSX Quantum per each EGU - for operation control; tons/yr 168: None; tons/yr 172: None; lbs/MMBtu 210: 0.771; lbs/MMBtu 211: 0.81; lbs/MMBtu 212: 0.7305; ppm 213: 129.3684
8303-01 | FirstLight | 10 |  | 1: 10; 2: 3; 3: FirstLight Hydro Generating Company; 4: FirstLight; 5: 8303; 6: Tunnel; 7: Tunnel Road Preston 10; 10: Tunnel Road Preston 10; 11: 10; 12: 10; 13: 557; 14: Combustion Turbine; 15: 1; 16: 1; 17: 1; 18: 8303-01; 19: Single turbine; 32: NOx RACT Compliance; 33: 22a-174-22c (CAIR); 34: 2011-04-29; 35: 2014-05-31; 36: 2011-01-11; 37: 2011-01-14; 47: Preston; 48: 150; 49: - / - / 150 / -; 50: CL&P Tunnel Preston Substation; 51: Preston, CT 06365; 52: FirstLight Hydro Generating Company (Owner); 53: FirstLight Hydro Generating Company (Owner) (Started Oct 19, 2010); Yr 56: 2010; Yr 58: First Light Power Resources; Yr 61: James A. Ginnetti; Yr 62: VP Hydro & Wind; Yr 63: James A. Ginnetti; Yr 64: VP Hydro & Wind; Yr 65: One Corporate Center 20 Church St, Hartford CT 06103; Yr 69: Yes; Yr 70: TRC; Yr 74: TRC staff; Yr 75: 2010-11-01; Yr 80: Electric Utility; Yr 81: EGU; Yr 82: 4911; Yr 83: Electric Services; Yr 87: Pratt & Whitney; Yr 88: FT4-8; Yr 89: FT; Yr 90: Turbo-Jet combustion turbine; MW 92: 20; MW 93: 20; MWe 96: 19.3; MWe 98: 22.1; month 100: Jan; year 101: 1969; year 102: 1969-01-01; yrs 103: 57.5935; yrs 106: Kerosene K1 (aviation fuel) low sulfur max. 0.3% wdb; yrs 107: Jet Fuel A (Kerosene K1); yrs 131: Stack Test; MMBtu/hr 132: NA; lbs/MMBtu 133: 0.698; ppmvd 134: 119.6; ppmvd 135: per TA&O; lb/MMBtu 136: 0.72; lbs/MMBtu 141: 0.29; ppmvd 142: 75; lbs/MMBtu 144: 0.15; ppmvd 150: 2006-03-29; ppmvd 151: 2011-03-29; ppmvd 152: 4.9993; ppmvd 154: 2010; ppmvd 155: 6; hrs 156: 20; MMBtu 157: 4575; MWh 158: 301; tons/yr 159: 1.7; tons/yr 160: 2009; tons/yr 161: 6; hrs 162: 3; MMBtu 163: 808; MWh 164: 46; tons/yr 165: 0.3; tons/yr 166: 30% at peak load; tons/yr 168: None; hrs 201: 50; hrs 202: 45; MMBtu/hr 205: 249; MMBtu/yr 206: 12450; MMBtu 207: 12450; MMBtu 208: 12450; lbs/MMBtu 210: 0.698; lbs/MMBtu 211: 0.72; lbs/MMBtu 212: 0.736; ppm 213: 186.7072; tons/yr 214: 4.5816; tons/yr 215: 4.5816; tons/yr 216: 4.5816
8304-01 | NPU | TRBINE |  | 1: 11; 2: 4; 3: Norwich Public Utilities; 4: NPU; 5: 8304; 6: Norwich; 7: Rolls Royce Turbine; 10: Rolls Royce Turbine; 11: TRBINE; 12: TRBINE; 13: 581; 14: Combustion Turbine; 15: 1; 16: 1; 17: 1; 18: 8304-01; 19: Single turbine; 32: NOx RACT Compliance; 33: 22a-174-22c (CAIR); 34: 2010-04-28; 35: 2014-05-31; 36: 2011-04-19; 37: 2011-04-21; 40: 8119A; 45: 8119A; 47: Norwich; 48: 139; 49: - / - / 139 / -; 50: Norwich Public Untilities; 51: 16 South Golden Street Norwich, CT 06360; 52: City of Norwich; 53: Norwich Public Utilities (Owner/Operator); Yr 58: City of Norwich - Dept. of Public Untilities; Yr 59: 16 South Golden Street, Norwich, CT 06360; Yr 60: NPU; Yr 61: John F. Bilda; Yr 62: General Manager; Yr 63: Mark Greene; Yr 65: 16 South Golden Street, Norwich, CT 06360; Yr 66: (860) 823-4119; Yr 67: (860) 823-4172; Yr 69: Yes; Yr 70: TRC; Yr 74: TRC staff; Yr 75: 2011-02-01; Yr 80: Electric Utility; Yr 81: EGU; Yr 82: 4911; Yr 83: Electric Services; Yr 87: Rolls Royce; Yr 88: Olympus B; MW 92: 18.8; MW 93: 18.8; MWe 96: 15.5; MWe 98: 18.8; year 101: 1972; year 102: 1972-01-01; yrs 103: 54.5956; yrs 106: No. 2 oil; yrs 107: No. 2 oil; yrs 109: 1426; yrs 110: gal/hr; yrs 112: 198; yrs 113: per TRC Report; yrs 131: Stack Test; MMBtu/hr 132: 249; lbs/MMBtu 133: 0.553; ppmvd 134: 141.31; ppmvd 135: per TA&O; lb/MMBtu 136: 0.62; ppmvd 142: 75; lbs/MMBtu 144: 0.15; ppmvd 150: 2009-09-26; ppmvd 151: 2014-06-26; ppmvd 152: 4.7474; ppmvd 154: 2010; ppmvd 155: 6; hrs 156: 19; MMBtu 157: 4811; MWh 158: 327; tons/yr 159: 1.5; tons/yr 160: 2009; tons/yr 161: 6; hrs 162: 15; MMBtu 163: 3782; MWh 164: 225; tons/yr 165: 1.2; tons/yr 166: 30% at peak load; tons/yr 168: None; hr 174: 38; hr 178: more 19 hrs than EPA-CAIROS report; MMBtu/yr 179: 198; hr 188: 38; MMBtu/hr 193: 198; hrs 201: 50; hrs 202: 38; MMBtu/hr 205: 198; MMBtu/yr 206: 9900; MMBtu 207: 9900; MMBtu 208: 9900; lbs/MMBtu 210: 0.553; lbs/MMBtu 211: 0.62; lbs/MMBtu 212: 0.553; ppm 213: 141.31; tons/yr 214: 2.7374; tons/yr 215: 2.7374; tons/yr 216: 3.069
8301-01 | PSEG | BHB4 |  | 1: 12; 2: 5; 3: PSEG Power LLC, PSEG Fossil LLC, PSEG Power Connecticut; 4: PSEG; 5: 8301; 6: Bridgeport Harbor Station; 7: Bridgeport Harbor Station 4; 10: Bridgeport Harbor Station (BHS) Unit No. 4; 11: BHB4; 12: BHB4; 13: 568; 14: Combustion Turbine; 15: 1; 16: 1; 17: 1; 18: 8301-01; 19: Single turbine; 20: Registration; 21: R-0166; 23: None; 29: 015-0217-TV; 30: 2009-09-16; 31: 2012-02-02; 32: NOx RACT Compliance; 33: 22a-174-22c (CAIR); 34: 2010-04-30; 35: 2014-05-31; 36: 2011-01-25; 37: 2011-01-27; 40: 8244; 47: Bridgeport; 48: 15; 49: - / - / 015 / -; 50: Bridgeport Harbor Station (BHS); 51: 1 Atlantic Street, Bridgeport, CT 06604; 52: PSEG Power LLC; 53: PSEG Power Connecticut, LLC (Owner/Operator); Yr 58: PSEG Fossil LLC; Yr 60: PSEG; Yr 61: Michael Stagliola; Yr 62: Plant Manager, New England Stations; Yr 63: Robert Silvestri; Yr 66: (203) 551-6032; Yr 69: Yes; Yr 70: PSEG Fossil LLC; Yr 75: 2011-01-25; Yr 76: 0; Yr 80: Electric Utility; Yr 81: EGU; Yr 82: 4911; Yr 83: Electric Services; Yr 84: Used during peak energy demand periods; Yr 85: burning waste aviation fuel; Yr 87: Pratt & Whitney; Yr 88: FT-4A-8LI; Yr 89: FT; Yr 90: Turbo-Jet combustion turbine; MW 92: 22; MW 93: 602; month 100: Jan; year 101: 1967; year 102: 1967-01-15; yrs 103: 59.5566; yrs 106: Kerosene K1 (aviation fuel Jet "A") low sulfur max. 0.3% wdb; yrs 107: Jet Fuel A (Kerosene K1); yrs 131: Stack Test; MMBtu/hr 132: 287; lbs/MMBtu 133: 0.709; ppmvd 134: 186.17; ppmvd 135: per TA&O; lb/MMBtu 136: 0.73; ppmvd 142: 75; lbs/MMBtu 144: 0.15; ppmvd 150: 2010-01-19; ppmvd 151: 2015-01-19; ppmvd 152: 4.9993; ppmvd 154: 2010; ppmvd 155: 6; hrs 156: 11; MMBtu 157: 2026; MWh 158: 114; tons/yr 159: 0.7; tons/yr 160: 2009; tons/yr 161: 6; hrs 162: 8; MMBtu 163: 1962; MWh 164: 119; tons/yr 165: 0.7; tons/yr 168: None; lbs/MMBtu 210: 0.709; lbs/MMBtu 211: 0.73; lbs/MMBtu 212: 0.73; ppm 213: 186.17
8300-01 | NRG | BR10 |  | 1: 13; 2: 6; 3: NRG Energy, Inc; 4: NRG; 5: 8300; 6: Branford; 7: Boston Post Road Branford -10; 10: Boston Post Road Branford -10; 11: BR10; 12: 10; 13: 540; 14: Combustion Turbine; 15: 1; 16: 1; 17: 1; 18: 8300-01; 19: Single turbine; 20: Registration; 21: R-014-0008; 23: None; 24: R-141-000-401; 32: NOx RACT Compliance; 33: 22a-174-22(e) & (f) (CAIR); 35: 2014-05-31; 36: 2011-04-25; 47: Branford; 48: 14; 49: - / - / 014 / -; 50: Boston Post Road Branford; 51: Boston Post Road Branford; 52: NRG Energy, Inc; 53: Connecticut Jet Power, LLC (Owner/Operator); Yr 58: NRG Energy, Inc.; Yr 59: P.O. Box 1001, 1866 River Rd, Middletown CT 06547; Yr 60: NRG; Yr 61: Cynthia L. Karlic; Yr 62: Regional Environmental Manager; Yr 65: P.O. Box 1001 1866 River Rd, Middletown CT 06547; Yr 69: Yes; Yr 70: NRG Energy, Inc.; Yr 78: Evaluate control technology options to reduce the current NOx level to 42 ppmvd at 15% oxygen (0.15 lbs/MMBtu); Yr 79: wrong Registration # on page 5; Yr 80: Electric Utility; Yr 81: EGU; Yr 82: 4911; Yr 83: Electric Services; Yr 84: Unit projected / scheduled operation is for ISO-NE required DR; Yr 87: Pratt & Whitney; Yr 88: FT4-A8; Yr 89: FT; Yr 90: Pratt & Whitney FT4 Aeroderivative Gas Turbine; MW 92: 20; MW 93: 20; MMBtu/hr 95: Electric Machinery 21,875 MVA Generator (104ºF Rating); MWe 96: 17-18 MW; MWe 97: at 90ºF; MWe 98: 22; MWe 99: at 20ºF; month 100: Jul; year 101: 1969; year 102: 1969-07-01; yrs 103: 57.098; yrs 104: Unmanned unit, operated remotely; yrs 105: Ultra low sulfur kerosene oil (ULSD); yrs 106: other oil; yrs 107: Ultra low sulfur kerosene oil (ULSD); yrs 131: Stack Test; MMBtu/hr 132: 256; lbs/MMBtu 133: 0.726; ppmvd 135: per TA&O; lb/MMBtu 136: 0.8; lbs/MMBtu 141: 0.29; lbs/MMBtu 144: 0.15; lbs/MMBtu 147: 0.15; ppmvd 150: 2006-08-10; ppmvd 151: 2011-08-10; ppmvd 152: 4.9993; ppmvd 154: 2010; ppmvd 155: 6; hrs 156: 39; MMBtu 157: 9750; MWh 158: 512; tons/yr 159: 5.9; tons/yr 160: 2009; tons/yr 161: 6; hrs 162: 2; MMBtu 163: 525; MWh 164: 20; tons/yr 165: 0.3; tons/yr 166: ISO-NE DR & quick start testing - 3 hrs per season; tons/yr 168: None, per NRG report; Water Injection since Jun 2008 per EPA.; tons/yr 172: Stack Tests; tons/yr 173: 2010; hr 174: 38.8; hr 175: 30.3; hr 176: 8.5; hr 178: same as EPA-CAIROS report; MMBtu/yr 180: 10110; MMBtu/yr 181: same as EPA-CAIROS report, within ±10%; MMBtu/yr 186: 0.4%; MMBtu/yr 187: 2009; hr 188: 19.1; hr 189: 6.1; hr 190: 15.6; hr 191: 21.7; hr 192: more 17 hrs than EPA-CAIROS report; MMBtu/yr 194: 5360; MMBtu/yr 195: reported more 921% MMBtu/hr than EPA-CAIROS report; MWh 200: 0.2%; hrs 201: 29; hrs 202: 28.95; hrs 203: 16.91; hrs 204: 12.05; MMBtu/yr 206: 7735; MMBtu 207: 7735; MMBtu 208: 7735; lbs/MMBtu 210: 0.726; lbs/MMBtu 211: 0.8; lbs/MMBtu 212: 0.8; tons/yr 214: 3.4; tons/yr 215: 3.4; tons/yr 216: 3.094
8300-02 |  | CC10 |  | 1: 14; 2: 7; 4: NRG; 5: 8300; 6: Cos Cob; 7: Cos Cob 10-12; 10: Sound Shore Drive Greenwich-10; 11: CC10; 12: 10; 13: 542; 14: Combustion Turbine; 15: 3; 16: 1; 17: 2; 18: 8300-02; 19: Single turbine; 20: Registration; 21: R-067-0052; 23: None; 24: R-067-0052; 32: NOx RACT Compliance; 33: 22a-174-22(f) (CAIR); 35: 2014-05-31; 36: 2011-04-25; 47: Greenwich; 48: 67; 49: - / - / 067 / -; 50: Sound Shore Drive Greenwich; 51: Sound Shore Drive, Cos Cob; 52: NRG Energy, Inc; 53: Connecticut Jet Power, LLC (Owner/Operator); Yr 58: NRG Energy, Inc.; Yr 59: P.O. Box 1001, 1866 River Rd, Middletown CT 06547; Yr 60: NRG; Yr 61: Cynthia L. Karlic; Yr 62: Regional Environmental Manager; Yr 65: P.O. Box 1001 1866 River Rd, Middletown CT 06547; Yr 69: Yes; Yr 70: NRG Energy, Inc.; Yr 78: Evaluate control technology options to reduce the current NOx level to 42 ppmvd at 15% oxygen (0.15 lbs/MMBtu); Yr 80: Electric Utility; Yr 81: EGU; Yr 82: 4911; Yr 83: Electric Services; Yr 84: 5 units on site for ISO-NE required DR; Yr 87: Pratt & Whitney; Yr 88: FT4-A9; Yr 89: FT; Yr 90: Pratt & Whitney FT4 Vintage A9; MW 92: 20; MW 93: 100; year 101: 1969; year 102: 1969-06-01; yrs 103: 57.1801; yrs 104: Unmanned unit, operated remotely; yrs 105: Ultra low sulfur kerosene oil (ULSD); yrs 106: other oil; yrs 107: Ultra low sulfur kerosene oil (ULSD); yrs 131: Stack Test; MMBtu/hr 132: 256; lbs/MMBtu 133: 0.192; ppmvd 135: per TA&O; lb/MMBtu 136: 0.22; lbs/MMBtu 144: 0.15; lbs/MMBtu 147: 0.15; ppmvd 150: 2008-11-19; ppmvd 151: 2013-11-19; ppmvd 152: 4.9993; ppmvd 154: 2010; ppmvd 155: 6; hrs 156: 44; MMBtu 157: 11038; MWh 158: 677; tons/yr 159: 6.6; tons/yr 160: 2009; tons/yr 161: 6; hrs 162: 8; MMBtu 163: 1968; MWh 164: 139; tons/yr 165: 1.2; tons/yr 166: ISO-NE DR & quick start testing - 3 hrs per season; tons/yr 168: Water Injection; tons/yr 172: Stack Tests; tons/yr 173: 2010; hr 174: 1 - 53; MMBtu/yr 186: 0.1%; MMBtu/yr 187: 2009; hr 188: 1 - 53; MWh 200: 0.1%; lbs/MMBtu 210: 0.192; lbs/MMBtu 211: 0.22; lbs/MMBtu 212: 0.22
8300-03 |  | CC11 |  | 1: 15; 4: NRG; 5: 8300; 6: Cos Cob; 10: Sound Shore Drive Greenwich-11; 11: CC11; 12: 11; 13: 542; 14: Combustion Turbine; 15: 3; 16: 1; 17: 3; 18: 8300-03; 19: Single turbine; 20: Registration; 21: R-067-0053; 23: None; 24: R-067-0053; 32: NOx RACT Compliance; 33: 22a-174-22(f) (CAIR); 35: 2014-05-31; 36: 2011-04-25; 47: Greenwich; 48: 67; 49: - / - / 067 / -; 50: Sound Shore Drive Greenwich; 51: Sound Shore Drive, Cos Cob; 52: NRG Energy, Inc; 53: Connecticut Jet Power, LLC (Owner/Operator); Yr 58: NRG Energy, Inc.; Yr 59: P.O. Box 1001, 1866 River Rd, Middletown CT 06547; Yr 60: NRG; Yr 61: Cynthia L. Karlic; Yr 62: Regional Environmental Manager; Yr 65: P.O. Box 1001 1866 River Rd, Middletown CT 06547; Yr 69: Yes; Yr 70: NRG Energy, Inc.; Yr 78: Evaluate control technology options to reduce the current NOx level to 42 ppmvd at 15% oxygen (0.15 lbs/MMBtu); Yr 80: Electric Utility; Yr 81: EGU; Yr 82: 4911; Yr 83: Electric Services; Yr 84: 5 units on site for ISO-NE required DR; Yr 87: Pratt & Whitney; Yr 88: FT4-A9; Yr 89: FT; Yr 90: Pratt & Whitney FT4 Vintage A9; MW 92: 20; year 101: 1969; year 102: 1969-06-01; yrs 103: 57.1801; yrs 104: Unmanned unit, operated remotely; yrs 105: Ultra low sulfur kerosene oil (ULSD); yrs 106: other oil; yrs 107: Ultra low sulfur kerosene oil (ULSD); yrs 131: Stack Test; MMBtu/hr 132: 256; lbs/MMBtu 133: 0.185; ppmvd 135: per TA&O; lb/MMBtu 136: 0.22; lbs/MMBtu 144: 0.15; lbs/MMBtu 147: 0.15; ppmvd 150: 2008-11-19; ppmvd 151: 2013-11-19; ppmvd 152: 4.9993; ppmvd 154: 2010; ppmvd 155: 6; hrs 156: 40; MMBtu 157: 10085; MWh 158: 619; tons/yr 159: 6.1; tons/yr 160: 2009; tons/yr 161: 6; hrs 162: 6; MMBtu 163: 1465; MWh 164: 102; tons/yr 165: 0.9; tons/yr 166: ISO-NE DR & quick start testing - 3 hrs per season; tons/yr 168: Water Injection; tons/yr 172: Stack Tests; tons/yr 173: 2010; hr 174: 1 - 53; MMBtu/yr 186: 0.1%; MMBtu/yr 187: 2009; hr 188: 1 - 53; MWh 200: 0.1%; lbs/MMBtu 210: 0.185; lbs/MMBtu 211: 0.22; lbs/MMBtu 212: 0.22
8300-04 |  | CC12 |  | 1: 16; 4: NRG; 5: 8300; 6: Cos Cob; 10: Sound Shore Drive Greenwich-12; 11: CC12; 12: 12; 13: 542; 14: Combustion Turbine; 15: 3; 16: 1; 17: 4; 18: 8300-04; 19: Single turbine; 20: Registration; 21: R-067-0054; 23: None; 24: R-067-0054; 32: NOx RACT Compliance; 33: 22a-174-22(f) (CAIR); 35: 2014-05-31; 36: 2011-04-25; 47: Greenwich; 48: 67; 49: - / - / 067 / -; 50: Sound Shore Drive Greenwich; 51: Sound Shore Drive, Cos Cob; 52: NRG Energy, Inc; 53: Connecticut Jet Power, LLC (Owner/Operator); Yr 58: NRG Energy, Inc.; Yr 59: P.O. Box 1001, 1866 River Rd, Middletown CT 06547; Yr 60: NRG; Yr 61: Cynthia L. Karlic; Yr 62: Regional Environmental Manager; Yr 65: P.O. Box 1001 1866 River Rd, Middletown CT 06547; Yr 69: Yes; Yr 70: NRG Energy, Inc.; Yr 78: Evaluate control technology options to reduce the current NOx level to 42 ppmvd at 15% oxygen (0.15 lbs/MMBtu); Yr 80: Electric Utility; Yr 81: EGU; Yr 82: 4911; Yr 83: Electric Services; Yr 84: 5 units on site for ISO-NE required DR; Yr 87: Pratt & Whitney; Yr 88: FT4-A9; Yr 89: FT; Yr 90: Pratt & Whitney FT4 Vintage A9; MW 92: 20; year 101: 1969; year 102: 1969-06-01; yrs 103: 57.1801; yrs 104: Unmanned unit, operated remotely; yrs 105: Ultra low sulfur kerosene oil (ULSD); yrs 106: other oil; yrs 107: Ultra low sulfur kerosene oil (ULSD); yrs 131: Stack Test; MMBtu/hr 132: 256; lbs/MMBtu 133: 0.194; ppmvd 135: per TA&O; lb/MMBtu 136: 0.22; lbs/MMBtu 144: 0.15; lbs/MMBtu 147: 0.15; ppmvd 150: 2008-11-19; ppmvd 151: 2013-11-19; ppmvd 152: 4.9993; ppmvd 154: 2010; ppmvd 155: 6; hrs 156: 51; MMBtu 157: 12848; MWh 158: 790; tons/yr 159: 7.7; tons/yr 160: 2009; tons/yr 161: 6; hrs 162: 7; MMBtu 163: 1780; MWh 164: 131; tons/yr 165: 1.1; tons/yr 166: ISO-NE DR & quick start testing - 3 hrs per season; tons/yr 168: Water Injection; tons/yr 172: Stack Tests; tons/yr 173: 2010; hr 174: 1 - 53; MMBtu/yr 186: 0.1%; MMBtu/yr 187: 2009; hr 188: 1 - 53; MWh 200: 0.1%; lbs/MMBtu 210: 0.194; lbs/MMBtu 211: 0.22; lbs/MMBtu 212: 0.22
8300-05 |  | CC13 |  | 1: 17; 2: 8; 4: NRG; 5: 8300; 6: Cos Cob; 7: Cos Cob 13-14; 10: Sound Shore Drive Greenwich-13; 11: CC13; 12: 13; 13: 542; 14: Combustion Turbine; 15: 2; 16: 1; 17: 5; 18: 8300-05; 19: Single turbine; 20: NSR Permit; 21: P-067-0097; 23: None; 24: P-067-0097; 32: NOx RACT Compliance; 33: 22a-174-22(f) (CAIR); 35: 2014-05-31; 36: 2011-04-25; 47: Greenwich; 48: 67; 49: - / - / 067 / -; 50: Sound Shore Drive Greenwich; 51: Sound Shore Drive, Cos Cob; 52: NRG Energy, Inc; 53: Connecticut Jet Power, LLC (Owner/Operator); Yr 58: NRG Energy, Inc.; Yr 59: P.O. Box 1001, 1866 River Rd, Middletown CT 06547; Yr 60: NRG; Yr 61: Cynthia L. Karlic; Yr 62: Regional Environmental Manager; Yr 65: P.O. Box 1001 1866 River Rd, Middletown CT 06547; Yr 69: Yes; Yr 70: NRG Energy, Inc.; Yr 78: Evaluate control technology options to reduce the current NOx level to 42 ppmvd at 15% oxygen (0.15 lbs/MMBtu); Yr 80: Electric Utility; Yr 81: EGU; Yr 82: 4911; Yr 83: Electric Services; Yr 84: 5 units on site for ISO-NE required DR; Yr 87: Pratt & Whitney; Yr 88: FT4-A9; Yr 89: FT; Yr 90: Pratt & Whitney FT4 Vintage A9; MW 92: 20; year 101: 1969; year 102: 1969-06-01; yrs 103: 57.1801; yrs 104: Unmanned unit, operated remotely; yrs 105: Ultra low sulfur kerosene oil (ULSD); yrs 106: other oil Natural Gas; yrs 107: Ultra low sulfur kerosene oil (ULSD); yrs 115: Natural Gas; yrs 131: Stack Test; MMBtu/hr 132: 256; lbs/MMBtu 133: 0.194; ppmvd 135: per TA&O; lb/MMBtu 136: 0.22; lbs/MMBtu 144: 0.15; lbs/MMBtu 147: 0.15; ppmvd 150: 2008-11-19; ppmvd 151: 2013-11-19; ppmvd 152: 4.9993; ppmvd 154: 2010; ppmvd 155: 6; hrs 156: 35; MMBtu 157: 10832; MWh 158: 476; tons/yr 159: 6.5; tons/yr 160: 2009; tons/yr 161: 6; hrs 162: 8; MMBtu 163: 2602; MWh 164: 155; tons/yr 165: 1.6; tons/yr 166: ISO-NE DR & quick start testing - 3 hrs per season; tons/yr 168: Water Injection; tons/yr 172: Stack Tests; tons/yr 173: 2010; hr 174: 1 - 53; MMBtu/yr 186: 0.1%; MMBtu/yr 187: 2009; hr 188: 1 - 53; MWh 200: 0.1%; lbs/MMBtu 210: 0.194; lbs/MMBtu 211: 0.22; lbs/MMBtu 212: 0.22
8300-06 |  | CC14 |  | 1: 18; 4: NRG; 5: 8300; 6: Cos Cob; 10: Sound Shore Drive Greenwich-14; 11: CC14; 12: 14; 13: 542; 14: Combustion Turbine; 15: 2; 16: 1; 17: 6; 18: 8300-06; 19: Single turbine; 20: NSR Permit; 21: P-067-0098; 23: None; 24: P-067-0098; 32: NOx RACT Compliance; 33: 22a-174-22(f) (CAIR); 35: 2014-05-31; 36: 2011-04-25; 47: Greenwich; 48: 67; 49: - / - / 067 / -; 50: Sound Shore Drive Greenwich; 51: Sound Shore Drive, Cos Cob; 52: NRG Energy, Inc; 53: Connecticut Jet Power, LLC (Owner/Operator); Yr 58: NRG Energy, Inc.; Yr 59: P.O. Box 1001, 1866 River Rd, Middletown CT 06547; Yr 60: NRG; Yr 61: Cynthia L. Karlic; Yr 62: Regional Environmental Manager; Yr 65: P.O. Box 1001 1866 River Rd, Middletown CT 06547; Yr 69: Yes; Yr 70: NRG Energy, Inc.; Yr 78: Evaluate control technology options to reduce the current NOx level to 42 ppmvd at 15% oxygen (0.15 lbs/MMBtu); Yr 80: Electric Utility; Yr 81: EGU; Yr 82: 4911; Yr 83: Electric Services; Yr 84: 5 units on site for ISO-NE required DR; Yr 87: Pratt & Whitney; Yr 88: FT4-A9; Yr 89: FT; Yr 90: Pratt & Whitney FT4 Vintage A9; MW 92: 20; year 101: 1969; year 102: 1969-06-01; yrs 103: 57.1801; yrs 104: Unmanned unit, operated remotely; yrs 105: Ultra low sulfur kerosene oil (ULSD); yrs 106: other oil Natural Gas; yrs 107: Ultra low sulfur kerosene oil (ULSD); yrs 115: Natural Gas; yrs 131: Stack Test; MMBtu/hr 132: 256; lbs/MMBtu 133: 0.171; ppmvd 135: per TA&O; lb/MMBtu 136: 0.22; lbs/MMBtu 144: 0.15; lbs/MMBtu 147: 0.15; ppmvd 150: 2008-11-19; ppmvd 151: 2013-11-19; ppmvd 152: 4.9993; ppmvd 154: 2010; ppmvd 155: 6; hrs 156: 42; MMBtu 157: 12967; MWh 158: 604; tons/yr 159: 7.8; tons/yr 160: 2009; tons/yr 161: 6; hrs 162: 13; MMBtu 163: 4118; MWh 164: 209; tons/yr 165: 2.5; tons/yr 166: ISO-NE DR & quick start testing - 3 hrs per season; tons/yr 168: Water Injection; tons/yr 172: Stack Tests; tons/yr 173: 2010; hr 174: 1 - 53; MMBtu/yr 186: 0.1%; MMBtu/yr 187: 2009; hr 188: 1 - 53; MWh 200: 0.1%; lbs/MMBtu 210: 0.171; lbs/MMBtu 211: 0.22; lbs/MMBtu 212: 0.22
8300-07 |  | FD10 |  | 1: 19; 2: 9; 4: NRG; 5: 8300; 6: Franklin Drive; 7: Franklin Drive Torrington-10; 10: Franklin Drive Torrington-10; 11: FD10; 12: 10; 13: 561; 14: Combustion Turbine; 15: 1; 16: 1; 17: 7; 18: 8300-07; 19: Single turbine; 20: Registration; 21: R-183-0049; 23: None; 24: R-108-100-2401; 32: NOx RACT Compliance; 33: 22a-174-22(e) & (f) (CAIR); 35: 2014-05-31; 36: 2011-04-25; 47: Torrington; 48: 183; 49: - / - / 183 / -; 50: Franklin Drive Torrington; 51: Franklin Drive Torrington; 52: NRG Energy, Inc; 53: Connecticut Jet Power, LLC (Owner/Operator); Yr 58: NRG Energy, Inc.; Yr 59: P.O. Box 1001, 1866 River Rd, Middletown CT 06547; Yr 60: NRG; Yr 61: Cynthia L. Karlic; Yr 62: Regional Environmental Manager; Yr 65: P.O. Box 1001 1866 River Rd, Middletown CT 06547; Yr 69: Yes; Yr 70: NRG Energy, Inc.; Yr 78: Evaluate control technology options to reduce the current NOx level to 42 ppmvd at 15% oxygen (0.15 lbs/MMBtu); Yr 80: Electric Utility; Yr 81: EGU; Yr 82: 4911; Yr 83: Electric Services; Yr 84: Unit projected / scheduled operation is for ISO-NE required DR; Yr 87: Pratt & Whitney; Yr 88: FT4-A8; Yr 89: FT; Yr 90: Pratt & Whitney FT4 Aeroderivative Gas Turbine; MW 92: 20; MW 93: 20; MMBtu/hr 95: Electric Machinery 21,875 MVA Generator (104ºF Rating); MWe 96: 17-18 MW; MWe 97: at 90ºF; MWe 98: 22; MWe 99: at 20ºF; month 100: Jan; year 101: 1969; year 102: 1969-01-01; yrs 103: 57.5935; yrs 104: Unmanned unit, operated remotely; yrs 105: Ultra low sulfur kerosene oil (ULSD); yrs 106: other oil Natural Gas; yrs 107: Ultra low sulfur kerosene oil (ULSD); yrs 131: Stack Test; MMBtu/hr 132: 256; lbs/MMBtu 133: 0.76; ppmvd 135: per TA&O; lb/MMBtu 136: 0.8; lbs/MMBtu 141: 0.29; lbs/MMBtu 144: 0.15; lbs/MMBtu 147: 0.15; ppmvd 150: 2005-10-25; ppmvd 151: 2010-10-25; ppmvd 152: 4.9993; ppmvd 153: Report Discrepency - Stack test rate of 0.68 MM/Btu and date Jun 17, 2010; ppmvd 154: 2010; ppmvd 155: 6; hrs 156: 46; MMBtu 157: 11515; MWh 158: 639; tons/yr 159: 6.9; tons/yr 160: 2009; tons/yr 161: 6; hrs 162: 5; MMBtu 163: 1145; MWh 164: 62; tons/yr 165: 0.7; tons/yr 166: ISO-NE DR & quick start testing - 3 hrs per season; tons/yr 168: None; tons/yr 172: Stack Tests; tons/yr 173: 2010; hr 174: 48.2; hr 175: 38.2; hr 176: 10; hr 178: more 2 hrs than EPA-CAIROS report; MMBtu/yr 180: 12010; MMBtu/yr 181: same as EPA-CAIROS report, within ±10%; MMBtu/yr 186: 0.55%; MMBtu/yr 187: 2009; hr 188: 29.3; hr 189: 3.5; hr 190: 25.8; hr 191: 29.3; hr 192: more 24 hrs than EPA-CAIROS report; MMBtu/yr 194: 7820; MMBtu/yr 195: reported more 583% MMBtu/hr than EPA-CAIROS report; MWh 200: 0.3%; hrs 201: 38.8; hrs 202: 38.75; hrs 203: 16.91; hrs 204: 12.05; MMBtu/yr 206: 9915; MMBtu 207: 9915; MMBtu 208: 9915; lbs/MMBtu 210: 0.76; lbs/MMBtu 211: 0.8; lbs/MMBtu 212: 0.8; tons/yr 214: 4.2; tons/yr 215: 4.2; tons/yr 216: 3.966
8300-08 |  | TT10 |  | 1: 20; 2: 10; 4: NRG; 5: 8300; 6: Torrington Terminal; 7: Torrington Terminal 10; 10: South Main Street Torrington-10; 11: TT10; 12: 10; 13: 565; 14: Combustion Turbine; 15: 1; 16: 1; 17: 8; 18: 8300-08; 19: Single turbine; 20: Registration; 21: R-183-0059; 23: None; 24: R-183-100-4301; 32: NOx RACT Compliance; 33: 22a-174-22(e) & (f) (CAIR); 35: 2014-05-31; 36: 2011-04-25; 47: Torrington; 48: 183; 49: - / - / 183 / -; 50: South Main Street Torrington; 51: South Main Street Torrington; 52: NRG Energy, Inc; 53: Connecticut Jet Power, LLC (Owner/Operator); Yr 58: NRG Energy, Inc.; Yr 59: P.O. Box 1001, 1866 River Rd, Middletown CT 06547; Yr 60: NRG; Yr 61: Cynthia L. Karlic; Yr 62: Regional Environmental Manager; Yr 65: P.O. Box 1001 1866 River Rd, Middletown CT 06547; Yr 69: Yes; Yr 70: NRG Energy, Inc.; Yr 78: Evaluate control technology options to reduce the current NOx level to 42 ppmvd at 15% oxygen (0.15 lbs/MMBtu); Yr 80: Electric Utility; Yr 81: EGU; Yr 82: 4911; Yr 83: Electric Services; Yr 84: Unit projected / scheduled operation is for ISO-NE required DR; Yr 87: Pratt & Whitney; Yr 88: FT4-A8; Yr 89: FT; Yr 90: Pratt & Whitney FT4 Aeroderivative Gas Turbine; MW 92: 20; MW 93: 20; MMBtu/hr 95: Electric Machinery 21,875 MVA Generator (104ºF Rating); MWe 96: 17-18 MW; MWe 97: at 90ºF; MWe 98: 22; MWe 99: at 20ºF; month 100: Jan; year 101: 1969; year 102: 1969-01-01; yrs 103: 57.5935; yrs 104: Unmanned unit, operated remotely; yrs 105: Ultra low sulfur kerosene oil (ULSD); yrs 106: other oil; yrs 107: Ultra low sulfur kerosene oil (ULSD); yrs 131: Stack Test; MMBtu/hr 132: 256; lbs/MMBtu 133: 0.68; ppmvd 135: per TA&O; lb/MMBtu 136: 0.8; lbs/MMBtu 141: 0.29; lbs/MMBtu 144: 0.15; lbs/MMBtu 147: 0.15; ppmvd 150: 2006-01-02; ppmvd 151: 2011-01-02; ppmvd 152: 4.9993; ppmvd 153: Report Discrepency - Stack test rate of 0.71 MM/Btu and date Jun 17, 2010; ppmvd 154: 2010; ppmvd 155: 6; hrs 156: 36; MMBtu 157: 9070; MWh 158: 468; tons/yr 159: 5.4; tons/yr 160: 2009; tons/yr 161: 6; hrs 162: 6; MMBtu 163: 1408; MWh 164: 91; tons/yr 165: 0.8; tons/yr 166: ISO-NE DR & quick start testing - 3 hrs per season; tons/yr 168: None; tons/yr 172: Stack Tests; tons/yr 173: 2010; hr 174: 34.8; hr 175: 28.2; hr 176: 6.7; hr 177: 34.9; hr 178: less -1 hrs than EPA-CAIROS report; MMBtu/yr 180: 10110; MMBtu/yr 181: reported more 11% MMBtu/hr than EPA-CAIROS report; MMBtu/yr 186: 0.4%; MMBtu/yr 187: 2009; hr 188: 24.3; hr 189: 5.1; hr 190: 19.1; hr 191: 24.2; hr 192: more 18 hrs than EPA-CAIROS report; MMBtu/yr 194: 6540; MMBtu/yr 195: reported more 364% MMBtu/hr than EPA-CAIROS report; MWh 200: 0.3%; hrs 201: 29.5; hrs 202: 29.55; hrs 203: 16.91; hrs 204: 12.05; MMBtu/yr 206: 8325; MMBtu 207: 8325; MMBtu 208: 8325; lbs/MMBtu 210: 0.68; lbs/MMBtu 211: 0.8; lbs/MMBtu 212: 0.8; tons/yr 214: 3.2; tons/yr 215: 3.2; tons/yr 216: 3.33
8300-09 |  | MD10 |  | 1: 21; 2: 11; 4: NRG; 5: 8300; 6: Middletown; 7: Middletown 10; 10: Middletown-10; 11: MD10; 12: 10; 13: 562; 14: Combustion Turbine; 15: 1; 16: 1; 17: 9; 18: 8300-09; 19: Single turbine; 20: Registration; 21: R-105-0102; 23: None; 24: R-104-0102; 32: NOx RACT Compliance; 33: 22a-174-22(e) & (f) (CAIR); 35: 2014-05-31; 36: 2011-04-25; 47: Middletown; 48: 104; 49: - / - / 104 / -; 50: Middletown Station; 51: River Road, Middletown; 52: NRG Energy, Inc; 53: Middletown Power, LLC (Owner/Operator); Yr 58: NRG Energy, Inc.; Yr 59: P.O. Box 1001, 1866 River Rd, Middletown CT 06547; Yr 60: NRG; Yr 61: Cynthia L. Karlic; Yr 62: Regional Environmental Manager; Yr 65: P.O. Box 1001 1866 River Rd, Middletown CT 06547; Yr 69: Yes; Yr 70: NRG Energy, Inc.; Yr 78: Evaluate control technology options to reduce the current NOx level to 42 ppmvd at 15% oxygen (0.15 lbs/MMBtu); Yr 80: Electric Utility; Yr 81: EGU; Yr 82: 4911; Yr 83: Electric Services; Yr 84: Unit projected / scheduled operation is for ISO-NE required DR; Yr 87: Pratt & Whitney; Yr 88: FT4-A8; Yr 89: FT; Yr 90: Pratt & Whitney FT4 Aeroderivative Gas Turbine; MW 92: 20; MW 93: 953; MMBtu/hr 95: Electric Machinery 21,875 MVA Generator (104ºF Rating); MWe 96: 17-18 MW; MWe 97: at 90ºF; MWe 98: 22; MWe 99: at 20ºF; month 100: Aug; year 101: 1966; year 102: 1966-08-01; yrs 103: 60.0138; yrs 105: Ultra low sulfur kerosene oil (ULSD); yrs 106: other oil; yrs 107: Ultra low sulfur kerosene oil (ULSD); yrs 131: Stack Test; MMBtu/hr 132: 256; lbs/MMBtu 133: 0.57; ppmvd 135: per TA&O; lb/MMBtu 136: 0.67; lbs/MMBtu 141: 0.29; lbs/MMBtu 144: 0.15; lbs/MMBtu 147: 0.15; ppmvd 150: 2006-06-20; ppmvd 151: 2011-06-20; ppmvd 152: 4.9993; ppmvd 154: 2010; ppmvd 155: 6; hrs 156: 95; MMBtu 157: 23750; MWh 158: 1275; tons/yr 159: 14.3; tons/yr 160: 2009; tons/yr 161: 6; hrs 162: 20; MMBtu 163: 5013; MWh 164: 243; tons/yr 165: 3; tons/yr 166: ISO-NE DR & quick start testing - 3 hrs per season; tons/yr 168: None; tons/yr 172: Stack Tests; tons/yr 173: 2010; hr 174: 107.9; hr 175: 80.6; hr 176: 27.3; hr 177: 107.9; hr 178: more 13 hrs than EPA-CAIROS report; MMBtu/yr 180: 19420; MMBtu/yr 181: less -18% MMBtu/hr than EPA-CAIROS report; MMBtu/yr 186: 1.2%; MMBtu/yr 187: 2009; hr 188: 92; hr 189: 23.6; hr 190: 68.4; hr 191: 92; hr 192: more 72 hrs than EPA-CAIROS report; MMBtu/yr 194: 22540; MMBtu/yr 195: reported more 350% MMBtu/hr than EPA-CAIROS report; MWh 200: 1%; hrs 201: 99.9; hrs 202: 99.95; hrs 203: 16.91; hrs 204: 12.05; MMBtu/yr 206: 20980; MMBtu 207: 20980; MMBtu 208: 20980; lbs/MMBtu 210: 0.57; lbs/MMBtu 211: 0.67; lbs/MMBtu 212: 0.67; tons/yr 214: 6.2; tons/yr 215: 6.2; tons/yr 216: 7.0283
8300-10 |  | NH10 |  | 1: 22; 2: 12; 4: NRG; 5: 8300; 6: Norwalk Harbor Station; 7: Norwalk Harbor Station 10; 10: Norwalk-10; 11: NH10; 12: 10; 13: 548; 14: Combustion Turbine; 15: 1; 16: 1; 17: 10; 18: 8300-10; 19: Single turbine; 20: Registration; 21: R-137-0032; 23: None; 24: R-137-0032; 32: NOx RACT Compliance; 33: 22a-174-22(e) & (f) (CAIR); 35: 2014-05-31; 36: 2011-04-25; 47: Norwalk; 48: 137; 49: - / - / 137 / -; 50: Norwalk Harbor Station; 51: Manresa island Avenue, South Norwalk; 52: NRG Energy, Inc; 53: Norwalk Power, LLC (Owner/Operator); Yr 58: NRG Energy, Inc.; Yr 59: P.O. Box 1001, 1866 River Rd, Middletown CT 06547; Yr 60: NRG; Yr 61: Cynthia L. Karlic; Yr 62: Regional Environmental Manager; Yr 65: P.O. Box 1001 1866 River Rd, Middletown CT 06547; Yr 69: Yes; Yr 70: NRG Energy, Inc.; Yr 78: Evaluate control technology options to reduce the current NOx level to 42 ppmvd at 15% oxygen (0.15 lbs/MMBtu); Yr 80: Electric Utility; Yr 81: EGU; Yr 82: 4911; Yr 83: Electric Services; Yr 84: Unit projected / scheduled operation is for ISO-NE required DR; Yr 87: Westinghouse; Yr 88: W191; Yr 90: Gas turbine; MW 92: 17; MW 93: 353; MMBtu/hr 95: Westinghouse; MWe 96: 14 MW; MWe 97: at 90ºF; MWe 98: 17 MW; MWe 99: at 20ºF; month 100: Oct; year 101: 1966; year 102: 1966-10-01; yrs 103: 59.8468; yrs 105: No.2 Oil; yrs 106: other oil; yrs 107: No.2 Oil; yrs 131: Stack Test; MMBtu/hr 132: 256; lbs/MMBtu 133: 0.514; ppmvd 135: per TA&O; lb/MMBtu 136: 0.52; lbs/MMBtu 141: 0.29; lbs/MMBtu 144: 0.15; lbs/MMBtu 147: 0.15; ppmvd 150: 2010-01-26; ppmvd 151: 2015-01-26; ppmvd 152: 4.9993; ppmvd 154: 2010; ppmvd 155: 6; hrs 156: 22; MMBtu 157: 13; MWh 158: 216; tons/yr 160: 2009; tons/yr 161: 6; hrs 162: 6; MMBtu 163: 4; MWh 164: 55; tons/yr 166: ISO-NE DR & quick start testing - 3 hrs per season; tons/yr 168: None; tons/yr 172: Stack Tests; tons/yr 173: 2010; hr 174: 23.1; hr 175: 17.5; hr 176: 5.5; hr 177: 23; hr 178: more 1 hrs than EPA-CAIROS report; MMBtu/yr 180: 5310; MMBtu/yr 181: reported more 40746% MMBtu/hr than EPA-CAIROS report; MMBtu/yr 186: 0.3%; MMBtu/yr 187: 2009; hr 188: 5.9; hr 189: 4.1; hr 190: 1.8; hr 191: 5.9; hr 192: same as EPA-CAIROS report; MMBtu/yr 194: 1650; MMBtu/yr 195: reported more 41150% MMBtu/hr than EPA-CAIROS report; MWh 200: 0.07%; hrs 201: 14.5; hrs 202: 14.5; hrs 203: 16.91; hrs 204: 12.05; MMBtu/yr 206: 3480; MMBtu 207: 3480; MMBtu 208: 3480; lbs/MMBtu 210: 0.514; lbs/MMBtu 211: 0.52; lbs/MMBtu 212: 0.52; tons/yr 214: 1; tons/yr 215: 1; tons/yr 216: 0.9048
8300-11 |  | DV10 |  | 1: 23; 2: 13; 4: NRG; 5: 8300; 6: Devon; 7: Devon 10; 10: Devon-10; 11: DV10; 12: 10; 13: 544; 14: Combustion Turbine; 15: 1; 16: 1; 17: 11; 18: 8300-11; 19: Single turbine; 20: Registration; 21: R-105-0026; 23: None; 24: P-105-0026; 32: NOx RACT Compliance; 33: 22a-174-22(e) & (f) (CAIR); 35: 2014-05-31; 36: 2011-04-25; 47: Milford; 48: 105; 49: - / - / 105 / -; 50: Devon Station; 51: Naugatuck Avenue, Devon; 52: NRG Energy, Inc; 53: Devon Power, LLC (Owner/Operator); Yr 58: NRG Energy, Inc.; Yr 59: P.O. Box 1001, 1866 River Rd, Middletown CT 06547; Yr 60: NRG; Yr 61: Cynthia L. Karlic; Yr 62: Regional Environmental Manager; Yr 65: P.O. Box 1001 1866 River Rd, Middletown CT 06547; Yr 69: Yes; Yr 70: NRG Energy, Inc.; Yr 78: Evaluate control technology options to reduce the current NOx level to 42 ppmvd at 15% oxygen (0.15 lbs/MMBtu); Yr 80: Electric Utility; Yr 81: EGU; Yr 82: 4911; Yr 83: Electric Services; Yr 84: Unit projected / scheduled operation is for ISO-NE required DR; Yr 87: Pratt & Whitney; Yr 88: FT4-A8; Yr 89: FT; Yr 90: Pratt & Whitney FT4 Aeroderivative Gas Turbine; MW 92: 20; MW 93: 180; MMBtu/hr 95: Electric Machinery 21,875 MVA Generator (104ºF Rating); MWe 96: 17-18 MW; MWe 97: at 90ºF; MWe 98: 22; MWe 99: at 20ºF; month 100: Mar; year 101: 1988; year 102: 1988-03-01; yrs 103: 38.4313; yrs 105: Ultra low sulfur kerosene oil (ULSD); yrs 106: other oil; yrs 107: Ultra low sulfur kerosene oil (ULSD); yrs 131: Stack Test; MMBtu/hr 132: 256; lbs/MMBtu 133: 0.67; ppmvd 135: per TA&O; lb/MMBtu 136: 0.74; lbs/MMBtu 141: 0.29; lbs/MMBtu 144: 0.15; lbs/MMBtu 147: 0.15; ppmvd 150: 2011-02-28; ppmvd 151: 2016-03-31; ppmvd 152: 5.0869; ppmvd 153: Changed ST rate to last test as of Feb 28, 2011; ppmvd 154: 2010; ppmvd 155: 6; hrs 156: 24; MMBtu 157: 5575; MWh 158: 454; tons/yr 159: 3.3; tons/yr 160: 2009; tons/yr 161: 6; hrs 162: 4; MMBtu 163: 869; MWh 164: 65; tons/yr 165: 0.5; tons/yr 166: ISO-NE DR & quick start testing - 3 hrs per season; tons/yr 168: None; tons/yr 172: Stack Tests; tons/yr 173: 2010; hr 174: 30.8; hr 175: 24.2; hr 176: 6.6; hr 177: 30.8; hr 178: more 7 hrs than EPA-CAIROS report; MMBtu/yr 180: 7130; MMBtu/yr 181: reported more 28% MMBtu/hr than EPA-CAIROS report; MMBtu/yr 186: 0.35%; MMBtu/yr 187: 2009; hr 188: 10.3; hr 189: 3.4; hr 190: 6.9; hr 191: 10.3; hr 192: more 6 hrs than EPA-CAIROS report; MMBtu/yr 194: 2580; MMBtu/yr 195: reported more 197% MMBtu/hr than EPA-CAIROS report; MWh 200: 0.1%; hrs 201: 20.55; hrs 202: 20.55; hrs 203: 16.91; hrs 204: 12.05; MMBtu/yr 206: 4855; MMBtu 207: 4855; MMBtu 208: 4855; lbs/MMBtu 210: 0.67; lbs/MMBtu 211: 0.74; lbs/MMBtu 212: 0.74; tons/yr 214: 1.8; tons/yr 215: 1.8; tons/yr 216: 1.7963
8300-12 |  | DV11 |  | 1: 24; 2: 14; 4: NRG; 5: 8300; 6: Devon; 7: Devon 11-14; 10: Devon-11; 11: DV11; 12: 11; 13: 544; 14: Combustion Turbine; 15: 4; 16: 1; 17: 12; 18: 8300-12; 19: Single turbine; 20: NSR Permit; 21: P-105-0040; 23: None; 24: R-104-040; 32: NOx RACT Compliance; 33: 22a-174-22(f) (CAIR) on oil only; 35: 2014-05-31; 36: 2011-04-25; 47: Milford; 48: 105; 49: - / - / 105 / -; 50: Devon Station; 51: Naugatuck Avenue, Devon; 52: NRG Energy, Inc; 53: Devon Power, LLC (Owner/Operator); Yr 58: NRG Energy, Inc.; Yr 59: P.O. Box 1001, 1866 River Rd, Middletown CT 06547; Yr 60: NRG; Yr 61: Cynthia L. Karlic; Yr 62: Regional Environmental Manager; Yr 65: P.O. Box 1001 1866 River Rd, Middletown CT 06547; Yr 69: Yes; Yr 70: NRG Energy, Inc.; Yr 78: Evaluate control technology options to reduce the current NOx level to 42 ppmvd at 15% oxygen (0.15 lbs/MMBtu); Yr 80: Electric Utility; Yr 81: EGU; Yr 82: 4911; Yr 83: Electric Services; Yr 84: Four identical GE units and one P&W (DV10) on site for ISO-NE required DR; Yr 87: General Electric; Yr 88: LM6000PA; Yr 90: General Electric LM 6000 PA Dual Fuel; MW 92: 40; MMBtu/hr 95: General Electric 60 MVA Air Cooled Generator; MWe 96: 30; MWe 97: at 90ºF; MWe 98: 40; MWe 99: at 20ºF; month 100: Jun; year 101: 1996; year 102: 1996-06-01; yrs 103: 30.1794; yrs 105: Natural Gas and Ultra low sulfur kerosene oil (ULSD); yrs 106: other oil Natural Gas; yrs 107: ULSD oil; yrs 114: 0.130 to 0.171 lbs/MMBtu; yrs 115: Natural Gas; yrs 122: 0.052 to 0.090 lbs/MMBtu; yrs 131: CEM; MMBtu/hr 132: 394; lbs/MMBtu 133: 0.171; ppmvd 135: test rate (max) for ULSD per NRG report; lb/MMBtu 136: 0.171; lbs/MMBtu 144: 0.15; lbs/MMBtu 147: 0.15; ppmvd 154: 2010; ppmvd 155: 12; hrs 156: 107; MMBtu 157: 34493; MWh 158: 3341; tons/yr 159: 2.6; tons/yr 160: 2009; tons/yr 161: 12; hrs 162: 70; MMBtu 163: 24111; MWh 164: 2387; tons/yr 165: 2; tons/yr 166: ISO-NE DR & quick start testing - 3 hrs per season; tons/yr 168: HPWI; tons/yr 172: PEMS; tons/yr 173: 2010; hr 174: 98.5; hr 175: 77.2; hr 176: 21.3; hr 177: 98.5; hr 178: less -9 hrs than EPA-CAIROS report; MMBtu/yr 180: 33700; MMBtu/yr 181: same as EPA-CAIROS report, within ±10%; MMBtu/yr 186: 0.7 to 1.4%; MMBtu/yr 187: 2009; hr 188: 62.9; hr 189: 15.3; hr 190: 47.6; hr 191: 62.9; hr 192: less -7 hrs than EPA-CAIROS report; MMBtu/yr 194: 23900; MMBtu/yr 195: same as EPA-CAIROS report, within ±10%; MWh 200: 0.7 to 1.4%; hrs 201: 80.7; hrs 202: 80.7; hrs 203: 16.91; hrs 204: 12.05; MMBtu/yr 206: 28800; MMBtu 207: 125150; MMBtu 208: 31287.5; lbs/MMBtu 210: 0.171; lbs/MMBtu 211: 0.171; lbs/MMBtu 212: 0.171; tons/yr 214: 10.64; tons/yr 215: 2.66; tons/yr 216: 2.6751
8300-13 |  | DV12 |  | 1: 25; 4: NRG; 5: 8300; 6: Devon; 10: Devon-12; 11: DV12; 12: 12; 13: 544; 14: Combustion Turbine; 15: 4; 16: 1; 17: 13; 18: 8300-13; 19: Single turbine; 20: NSR Permit; 21: P-105-0041; 23: None; 24: R-104-041; 32: NOx RACT Compliance; 33: 22a-174-22(f) (CAIR) on oil only; 35: 2014-05-31; 36: 2011-04-25; 47: Milford; 48: 105; 49: - / - / 105 / -; 50: Devon Station; 51: Naugatuck Avenue, Devon; 52: NRG Energy, Inc; 53: Devon Power, LLC (Owner/Operator); Yr 58: NRG Energy, Inc.; Yr 59: P.O. Box 1001, 1866 River Rd, Middletown CT 06547; Yr 60: NRG; Yr 61: Cynthia L. Karlic; Yr 62: Regional Environmental Manager; Yr 65: P.O. Box 1001 1866 River Rd, Middletown CT 06547; Yr 69: Yes; Yr 70: NRG Energy, Inc.; Yr 78: Evaluate control technology options to reduce the current NOx level to 42 ppmvd at 15% oxygen (0.15 lbs/MMBtu); Yr 80: Electric Utility; Yr 81: EGU; Yr 82: 4911; Yr 83: Electric Services; Yr 84: Four identical GE units and one P&W (DV10) on site for ISO-NE required DR; Yr 87: General Electric; Yr 88: LM6000PA; Yr 90: General Electric LM 6000 PA Dual Fuel; MW 92: 40; MMBtu/hr 95: General Electric 60 MVA Air Cooled Generator; MWe 96: 30; MWe 97: at 90ºF; MWe 98: 40; MWe 99: at 20ºF; month 100: Jun; year 101: 1996; year 102: 1996-06-01; yrs 103: 30.1794; yrs 105: Natural Gas and Ultra low sulfur kerosene oil (ULSD); yrs 106: other oil Natural Gas; yrs 107: ULSD oil; yrs 114: 0.130 to 0.171 lbs/MMBtu; yrs 115: Natural Gas; yrs 122: 0.052 to 0.090 lbs/MMBtu; yrs 131: CEM; MMBtu/hr 132: 394; lbs/MMBtu 133: 0.171; ppmvd 135: test rate (max) for ULSD per NRG report; lb/MMBtu 136: 0.171; lbs/MMBtu 144: 0.15; lbs/MMBtu 147: 0.15; ppmvd 154: 2010; ppmvd 155: 12; hrs 156: 79; MMBtu 157: 25823; MWh 158: 2531; tons/yr 159: 1.7; tons/yr 160: 2009; tons/yr 161: 12; hrs 162: 66; MMBtu 163: 22459; MWh 164: 2202; tons/yr 165: 1.5; tons/yr 166: ISO-NE DR & quick start testing - 3 hrs per season; tons/yr 168: HPWI; tons/yr 172: PEMS; tons/yr 173: 2010; hr 174: 72.3; hr 175: 53.2; hr 176: 19.2; hr 177: 72.4; hr 178: less -7 hrs than EPA-CAIROS report; MMBtu/yr 180: 26600; MMBtu/yr 181: same as EPA-CAIROS report, within ±10%; MMBtu/yr 186: 0.7 to 1.4%; MMBtu/yr 187: 2009; hr 188: 58.2; hr 189: 11; hr 190: 47.2; hr 191: 58.2; hr 192: less -8 hrs than EPA-CAIROS report; MMBtu/yr 194: 21900; MMBtu/yr 195: same as EPA-CAIROS report, within ±10%; MWh 200: 0.7 to 1.4%; hrs 201: 65.3; hrs 202: 65.25; hrs 203: 32.1; hrs 204: 33.2; MMBtu/yr 206: 24250; MMBtu 208: 31287.5; lbs/MMBtu 210: 0.171; lbs/MMBtu 211: 0.171; lbs/MMBtu 212: 0.171; tons/yr 215: 2.66; tons/yr 216: 2.6751
8300-14 |  | DV13 |  | 1: 26; 4: NRG; 5: 8300; 6: Devon; 10: Devon-13; 11: DV13; 12: 13; 13: 544; 14: Combustion Turbine; 15: 4; 16: 1; 17: 14; 18: 8300-14; 19: Single turbine; 20: NSR Permit; 21: P-105-0042; 23: None; 24: R-104-042; 32: NOx RACT Compliance; 33: 22a-174-22(f) (CAIR) on oil only; 35: 2014-05-31; 36: 2011-04-25; 47: Milford; 48: 105; 49: - / - / 105 / -; 50: Devon Station; 51: Naugatuck Avenue, Devon; 52: NRG Energy, Inc; 53: Devon Power, LLC (Owner/Operator); Yr 58: NRG Energy, Inc.; Yr 59: P.O. Box 1001, 1866 River Rd, Middletown CT 06547; Yr 60: NRG; Yr 61: Cynthia L. Karlic; Yr 62: Regional Environmental Manager; Yr 65: P.O. Box 1001 1866 River Rd, Middletown CT 06547; Yr 69: Yes; Yr 70: NRG Energy, Inc.; Yr 78: Evaluate control technology options to reduce the current NOx level to 42 ppmvd at 15% oxygen (0.15 lbs/MMBtu); Yr 80: Electric Utility; Yr 81: EGU; Yr 82: 4911; Yr 83: Electric Services; Yr 84: Four identical GE units and one P&W (DV10) on site for ISO-NE required DR; Yr 87: General Electric; Yr 88: LM6000PA; Yr 90: General Electric LM 6000 PA Dual Fuel; MW 92: 40; MMBtu/hr 95: General Electric 60 MVA Air Cooled Generator; MWe 96: 30; MWe 97: at 90ºF; MWe 98: 40; MWe 99: at 20ºF; month 100: Jun; year 101: 1996; year 102: 1996-06-01; yrs 103: 30.1794; yrs 105: Natural Gas and Ultra low sulfur kerosene oil (ULSD); yrs 106: other oil Natural Gas; yrs 107: ULSD oil; yrs 114: 0.130 to 0.171 lbs/MMBtu; yrs 115: Natural Gas; yrs 122: 0.052 to 0.090 lbs/MMBtu; yrs 131: CEM; MMBtu/hr 132: 394; lbs/MMBtu 133: 0.171; ppmvd 135: test rate (max) for ULSD per NRG report; lb/MMBtu 136: 0.171; lbs/MMBtu 144: 0.15; lbs/MMBtu 147: 0.15; ppmvd 154: 2010; ppmvd 155: 12; hrs 156: 114; MMBtu 157: 37637; MWh 158: 3634; tons/yr 159: 3; tons/yr 160: 2009; tons/yr 161: 12; hrs 162: 93; MMBtu 163: 31591; MWh 164: 3120; tons/yr 165: 2.5; tons/yr 166: ISO-NE DR & quick start testing - 3 hrs per season; tons/yr 168: HPWI; tons/yr 172: PEMS; tons/yr 173: 2010; hr 174: 105.1; hr 175: 80; hr 176: 25.1; hr 177: 105.1; hr 178: less -9 hrs than EPA-CAIROS report; MMBtu/yr 180: 38400; MMBtu/yr 181: same as EPA-CAIROS report, within ±10%; MMBtu/yr 186: 0.7 to 1.4%; MMBtu/yr 187: 2009; hr 188: 83.9; hr 189: 16.9; hr 190: 66.9; hr 191: 83.8; hr 192: less -9 hrs than EPA-CAIROS report; MMBtu/yr 194: 32000; MMBtu/yr 195: same as EPA-CAIROS report, within ±10%; MWh 200: 0.7 to 1.4%; hrs 201: 94.5; hrs 202: 94.5; hrs 203: 48.4; hrs 204: 46; MMBtu/yr 206: 35200; MMBtu 208: 31287.5; lbs/MMBtu 210: 0.171; lbs/MMBtu 211: 0.171; lbs/MMBtu 212: 0.171; tons/yr 215: 2.66; tons/yr 216: 2.6751
8300-15 |  | DV14 |  | 1: 27; 4: NRG; 5: 8300; 6: Devon; 10: Devon-14; 11: DV14; 12: 14; 13: 544; 14: Combustion Turbine; 15: 4; 16: 1; 17: 15; 18: 8300-15; 19: Single turbine; 20: NSR Permit; 21: P-105-0043; 23: None; 24: R-104-043; 32: NOx RACT Compliance; 33: 22a-174-22(f) (CAIR) on oil only; 35: 2014-05-31; 36: 2011-04-25; 47: Milford; 48: 105; 49: - / - / 105 / -; 50: Devon Station; 51: Naugatuck Avenue, Devon; 52: NRG Energy, Inc; 53: Devon Power, LLC (Owner/Operator); Yr 58: NRG Energy, Inc.; Yr 59: P.O. Box 1001, 1866 River Rd, Middletown CT 06547; Yr 60: NRG; Yr 61: Cynthia L. Karlic; Yr 62: Regional Environmental Manager; Yr 65: P.O. Box 1001 1866 River Rd, Middletown CT 06547; Yr 69: Yes; Yr 70: NRG Energy, Inc.; Yr 78: Evaluate control technology options to reduce the current NOx level to 42 ppmvd at 15% oxygen (0.15 lbs/MMBtu); Yr 80: Electric Utility; Yr 81: EGU; Yr 82: 4911; Yr 83: Electric Services; Yr 84: Four identical GE units and one P&W (DV10) on site for ISO-NE required DR; Yr 87: General Electric; Yr 88: LM6000PA; Yr 90: General Electric LM 6000 PA Dual Fuel; MW 92: 40; MMBtu/hr 95: General Electric 60 MVA Air Cooled Generator; MWe 96: 30; MWe 97: at 90ºF; MWe 98: 40; MWe 99: at 20ºF; month 100: Jun; year 101: 1996; year 102: 1996-06-01; yrs 103: 30.1794; yrs 105: Natural Gas and Ultra low sulfur kerosene oil (ULSD); yrs 106: other oil Natural Gas; yrs 107: ULSD oil; yrs 114: 0.130 to 0.171 lbs/MMBtu; yrs 115: Natural Gas; yrs 122: 0.052 to 0.090 lbs/MMBtu; yrs 131: CEM; MMBtu/hr 132: 394; lbs/MMBtu 133: 0.171; ppmvd 135: test rate (max) for ULSD per NRG report; lb/MMBtu 136: 0.171; lbs/MMBtu 144: 0.15; lbs/MMBtu 147: 0.15; ppmvd 154: 2010; ppmvd 155: 12; hrs 156: 131; MMBtu 157: 41882; MWh 158: 4136; tons/yr 159: 3.3; tons/yr 160: 2009; tons/yr 161: 12; hrs 162: 91; MMBtu 163: 31304; MWh 164: 3150; tons/yr 165: 2.6; tons/yr 166: ISO-NE DR & quick start testing - 3 hrs per season; tons/yr 168: HPWI; tons/yr 172: PEMS; tons/yr 173: 2010; hr 174: 120.4; hr 175: 90.1; hr 176: 30.3; hr 177: 120.4; hr 178: less -11 hrs than EPA-CAIROS report; MMBtu/yr 180: 42400; MMBtu/yr 181: same as EPA-CAIROS report, within ±10%; MMBtu/yr 186: 0.7 to 1.4%; MMBtu/yr 187: 2009; hr 188: 82.5; hr 189: 14.2; hr 190: 68.3; hr 191: 82.5; hr 192: less -9 hrs than EPA-CAIROS report; MMBtu/yr 194: 31400; MMBtu/yr 195: same as EPA-CAIROS report, within ±10%; MWh 200: 0.7 to 1.4%; hrs 201: 101.4; hrs 202: 101.45; hrs 203: 52.2; hrs 204: 49.3; MMBtu/yr 206: 36900; MMBtu 208: 31287.5; lbs/MMBtu 210: 0.171; lbs/MMBtu 211: 0.171; lbs/MMBtu 212: 0.171; tons/yr 215: 2.66; tons/yr 216: 2.6751
8300-16 | NRG | MV10 |  | 1: 28; 2: 15; 3: NRG Energy, Inc; 4: NRG; 5: 8300; 6: Montville; 7: Montville 10 -11; 10: Montville-10; 11: MV10; 14: Diesel Engine; 15: 2; 16: 1; 17: 16; 18: 8300-16; 19: Single Diesel engine; 23: None; 24: R-107-0021; 32: NOx RACT Compliance; 33: 22a-174-22(e) (CAIR); 35: 2014-05-31; 36: 2011-04-25; 47: Montville; 48: 107; 49: - / - / 107 / -; 50: Montville Station; 51: Lathrop Road, Uncasville; 52: NRG Energy, Inc; Yr 58: NRG Energy, Inc.; Yr 59: P.O. Box 1001, 1866 River Rd, Middletown CT 06547; Yr 60: NRG; Yr 61: Cynthia L. Karlic; Yr 62: Regional Environmental Manager; Yr 65: P.O. Box 1001 1866 River Rd, Middletown CT 06547; Yr 69: Yes; Yr 70: NRG Energy, Inc.; Yr 78: Evaluate control technology options to reduce the current NOx level to 42 ppmvd at 15% oxygen (0.15 lbs/MMBtu); Yr 81: EGU; Yr 84: Unit projected scheduled operation is for ISO-NE required DR; Yr 87: General Motors; Yr 88: EMD 20-645-E4; Yr 90: General Motors EMD 20-645-E4 Diesel Engine; MW 92: 2.75; MW 93: 488.5; MMBtu/hr 95: General Motors EMD 3440 KVA; MWe 96: 2.7; MWe 97: at 90ºF; MWe 98: 2.7; MWe 99: at 20ºF; month 100: Jan; year 101: 1966; year 102: 1966-01-15; yrs 103: 60.5559; yrs 105: 0.05% sulfur distillate oil; yrs 106: other oil; yrs 107: 0.05% sulfur distillate oil; yrs 131: Stack Test; MMBtu/hr 132: 29; lbs/MMBtu 133: 3.09; ppmvd 135: per TA&O; lb/MMBtu 136: 3.11; lbs/MMBtu 141: 2.35; lbs/MMBtu 144: 0.15; ppmvd 150: 2006-03-24; ppmvd 151: 2011-03-24; ppmvd 152: 4.9993; tons/yr 166: ISO-NE DR & quick start testing - 3 hrs per season; tons/yr 168: None; tons/yr 172: Stack Test; tons/yr 173: 2010; hr 174: 338.5; hr 175: 98; hr 176: 22.3; hr 177: 120.3; MMBtu/yr 186: 1.6%; MMBtu/yr 187: 2009; hr 188: 133.4; hr 189: 19.6; hr 190: 21.6; hr 191: 41.2; MWh 200: 1.6%; hrs 201: 235.95; hrs 202: 235.95; lbs/MMBtu 210: 3.09; lbs/MMBtu 211: 3.11; lbs/MMBtu 212: 3.11; tons/yr 214: 12; tons/yr 215: 6
8300-17 |  | MV11 |  | 1: 29; 4: NRG; 5: 8300; 6: Montville; 10: Montville-11; 11: MV11; 14: Diesel Engine; 15: 2; 16: 1; 17: 17; 18: 8300-17; 19: Single Diesel engine; 23: None; 24: R-107-0022; 32: NOx RACT Compliance; 33: 22a-174-22(e) (CAIR); 35: 2014-05-31; 36: 2011-04-25; 47: Montville; 48: 107; 49: - / - / 107 / -; 50: Montville Station; 51: Lathrop Road, Uncasville; 52: NRG Energy, Inc; Yr 58: NRG Energy, Inc.; Yr 59: P.O. Box 1001, 1866 River Rd, Middletown CT 06547; Yr 60: NRG; Yr 61: Cynthia L. Karlic; Yr 62: Regional Environmental Manager; Yr 65: P.O. Box 1001 1866 River Rd, Middletown CT 06547; Yr 69: Yes; Yr 70: NRG Energy, Inc.; Yr 78: Evaluate control technology options to reduce the current NOx level to 42 ppmvd at 15% oxygen (0.15 lbs/MMBtu); Yr 81: EGU; Yr 84: Unit projected scheduled operation is for ISO-NE required DR; Yr 87: General Motors; Yr 88: EMD 20-645-E4; Yr 90: General Motors EMD 20-645-E4 Diesel Engine; MW 92: 2.75; MMBtu/hr 95: General Motors EMD 3440 KVA; MWe 96: 2.7; MWe 97: at 90ºF; MWe 98: 2.7; MWe 99: at 20ºF; month 100: Jan; year 101: 1966; year 102: 1966-01-15; yrs 103: 60.5559; yrs 105: 0.05% sulfur distillate oil; yrs 106: other oil; yrs 107: 0.05% sulfur distillate oil; yrs 131: Stack Test; MMBtu/hr 132: 29; lbs/MMBtu 133: 1.93; ppmvd 135: per TA&O; lb/MMBtu 136: 2.96; lbs/MMBtu 141: 2.35; lbs/MMBtu 144: 0.15; ppmvd 150: 2006-08-23; ppmvd 151: 2011-08-23; ppmvd 152: 4.9993; tons/yr 166: ISO-NE DR & quick start testing - 3 hrs per season; tons/yr 168: None; tons/yr 172: Stack Test; tons/yr 173: 2010; hr 174: 163.6; hr 175: 113.5; hr 176: 50.1; hr 177: 163.6; MMBtu/yr 186: 1.6%; MMBtu/yr 187: 2009; hr 188: 133.4; hr 189: 20.4; hr 190: 89.6; hr 191: 110; MWh 200: 1.6%; hrs 201: 148.5; hrs 202: 148.5; lbs/MMBtu 210: 1.93; lbs/MMBtu 211: 2.96; lbs/MMBtu 212: 2.96; tons/yr 215: 6
8306-01 | NRG | MD2 |  | 1: 30; 2: 16; 3: NRG Energy, Inc; 4: NRG; 5: 8306; 6: Middletown; 7: Middletown 2; 8: Middletown Station; 10: Middletown-2; 11: MD2; 12: 2; 13: 562; 14: Utility Boiler; 15: 1; 16: 1; 17: 1; 18: 8306-01; 19: Single utility boiler; 20: Registration; 21: R-104-0098; 24: R-104-0098; 32: NOx RACT Compliance; 33: 22a-174-22(f) (CAIR); 47: Middletown; 48: 104; 49: - / - / 104 / -; 50: Middletown; 52: NRG Energy, Inc; 53: Middletown Power, LLC (Owner/Operator); Yr 58: NRG Energy, Inc.; Yr 59: P.O. Box 1001, 1866 River Rd, Middletown CT 06547; Yr 60: NRG; Yr 61: Cynthia L. Karlic; Yr 62: Regional Environmental Manager; Yr 65: P.O. Box 1001 1866 River Rd, Middletown CT 06547; Yr 69: Yes; Yr 80: Electric Utility; Yr 81: EGU; Yr 82: 4911; Yr 83: Electric Services; Yr 87: Riley; Yr 88: Front fired; Yr 90: Front Fired Riley boiler; MW 92: 120; MW 93: 953; MMBtu/hr 94: 1295; MMBtu/hr 95: General Electric Steam Turbine; MWe 96: 117; MWe 97: at 90ºF; MWe 98: 120; MWe 99: at 20ºF; yrs 105: (0.3%) No. 6 oil; No. 2 for ignition only; Nat Gas; yrs 106: No. 6, No. 2, Nat Gas; yrs 107: No. 6 oil; yrs 114: 0.25; yrs 115: No. 2 oil; yrs 116: for ignition only (per operator); yrs 122: 0.2; yrs 123: Nat Gas; yrs 129: AEL of 0.15 non-ozone season average regardless of fuels burned; yrs 130: 0.2; MMBtu/hr 132: 1295; lb/MMBtu 136: 0.18; lb/MMBtu 138: 0.15; ppmvd 140: FLER (max) per NRG report; lbs/MMBtu 141: 0.25; ppmvd 143: Primary fuel (No. 6 residual oil) only. If other oil-fired is used a 0.200 lbs/MMBtu should be considered.; lbs/MMBtu 147: 0.15; ppmvd 149: regardless of fuels burned; ppmvd 154: 2010; ppmvd 155: 12; hrs 156: 2181; MMBtu 157: 1620374; MWh 158: 124995; tons/yr 159: 107.3; tons/yr 160: 2009; tons/yr 161: 12; hrs 162: 1196; MMBtu 163: 878712; MWh 164: 66397; tons/yr 165: 66.7; tons/yr 168: None; tons/yr 173: 2010; hr 174: 1766.7; hr 175: 1492.8; hr 176: 273.9; hr 177: 1766.7; hr 178: less -414 hrs than EPA-CAIROS report; MMBtu/yr 180: 1322860; MMBtu/yr 181: less -18% MMBtu/hr than EPA-CAIROS report; MMBtu/yr 182: 128043; MMBtu/yr 183: same as EPA-CAIROS report, within ±5%; MMBtu/yr 186: 12.5%; MMBtu/yr 187: 2009; hr 188: 895.5; hr 189: 525.9; hr 190: 369.6; hr 191: 895.5; hr 192: less -301 hrs than EPA-CAIROS report; MMBtu/yr 194: 712620; MMBtu/yr 195: less -19% MMBtu/hr than EPA-CAIROS report; MWh 196: 66427; MWh 197: same as EPA-CAIROS report, within ±5%; MWh 200: 6.5%; hrs 201: 1331.1; hrs 202: 1331.1; MMBtu/yr 206: 1017740; MMBtu 207: 1017740; MMBtu 208: 1017740; lbs/MMBtu 211: 0.18; lbs/MMBtu 212: 0.18; tons/yr 214: 91.6; tons/yr 215: 91.6; tons/yr 216: 91.5966
8306-02 |  | MD3 |  | 1: 31; 2: 17; 4: NRG; 5: 8306; 6: Middletown; 7: Middletown 3; 8: Middletown Station; 10: Middletown-3; 11: MD3; 12: 3; 13: 562; 14: Utility Boiler; 15: 1; 16: 1; 17: 2; 18: 8306-02; 19: Single utility boiler; 20: Registration; 21: R-104-0100; 24: R-104-0100; 32: NOx RACT Compliance; 33: 22a-174-22(f) (CAIR); 47: Middletown; 48: 104; 49: - / - / 104 / -; 50: Middletown; 52: NRG Energy, Inc; 53: Middletown Power, LLC (Owner/Operator); Yr 58: NRG Energy, Inc.; Yr 59: P.O. Box 1001, 1866 River Rd, Middletown CT 06547; Yr 60: NRG; Yr 61: Cynthia L. Karlic; Yr 62: Regional Environmental Manager; Yr 65: P.O. Box 1001 1866 River Rd, Middletown CT 06547; Yr 69: Yes; Yr 80: Electric Utility; Yr 81: EGU; Yr 82: 4911; Yr 83: Electric Services; Yr 87: Babcock and Wilcox; Yr 88: Cyclone boiler; Yr 90: B&W Cyclone Boiler; MW 92: 236; MMBtu/hr 94: 2370; MMBtu/hr 95: General Electric Steam Turbine; MWe 96: 236; MWe 97: at 90ºF; MWe 98: 245; MWe 99: at 20ºF; yrs 105: (0.3%) No. 6 oil; No. 2 for ignition only; Nat Gas; yrs 106: No. 6, No. 2, Nat Gas; yrs 107: No. 6 oil; yrs 114: 0.43; yrs 115: No. 2 oil; yrs 116: for ignition only (per operator); yrs 122: 0.43; yrs 123: Nat Gas; yrs 129: AEL of 0.15 non-ozone season average regardless of fuels burned; yrs 130: 0.43; MMBtu/hr 132: 2370; lb/MMBtu 136: 0.27; lb/MMBtu 138: 0.27; ppmvd 140: FLER (max) per NRG report; lbs/MMBtu 141: 0.43; ppmvd 143: During ozone season only; lbs/MMBtu 147: 0.15; ppmvd 149: regardless of fuels burned; ppmvd 154: 2010; ppmvd 155: 12; hrs 156: 1173; MMBtu 157: 1937944; MWh 158: 151235; tons/yr 159: 213.4; tons/yr 160: 2009; tons/yr 161: 12; hrs 162: 500; MMBtu 163: 754650; MWh 164: 67712; tons/yr 165: 105.1; tons/yr 168: None; tons/yr 173: 2010; hr 174: 1040.6; hr 175: 968.7; hr 176: 71.9; hr 177: 1040.6; hr 178: less -132 hrs than EPA-CAIROS report; MMBtu/yr 180: 1731940; MMBtu/yr 181: less -11% MMBtu/hr than EPA-CAIROS report; MMBtu/yr 182: 150420; MMBtu/yr 183: same as EPA-CAIROS report, within ±5%; MMBtu/yr 186: 7.3%; MMBtu/yr 187: 2009; hr 188: 421.5; hr 189: 257.8; hr 190: 163.7; hr 191: 421.5; hr 192: less -79 hrs than EPA-CAIROS report; MMBtu/yr 194: 734600; MMBtu/yr 195: same as EPA-CAIROS report, within ±10%; MWh 196: 66412; MWh 197: same as EPA-CAIROS report, within ±5%; MWh 200: 3.2%; hrs 201: 731.05; hrs 202: 731.05; MMBtu/yr 206: 1233270; MMBtu 207: 1233270; MMBtu 208: 1233270; lbs/MMBtu 211: 0.27; lbs/MMBtu 212: 0.27; tons/yr 214: 166.49; tons/yr 215: 166.49; tons/yr 216: 166.4914
8306-03 |  | MD4 |  | 1: 32; 2: 18; 4: NRG; 5: 8306; 6: Middletown; 7: Middletown 4; 8: Middletown Station; 10: Middletown-4; 11: MD4; 12: 4; 13: 562; 14: Utility Boiler; 15: 1; 16: 1; 17: 3; 18: 8306-03; 19: Single utility boiler; 20: Registration; 21: -; 24: P-104-0003; 29: P-104-0003; 32: NOx RACT Compliance; 33: 22a-174-22(f) (CAIR); 47: Middletown; 48: 104; 49: - / - / 104 / -; 50: Middletown; 52: NRG Energy, Inc; 53: Middletown Power, LLC (Owner) / NRG Energy, Inc (Operator; Yr 58: NRG Energy, Inc.; Yr 59: P.O. Box 1001, 1866 River Rd, Middletown CT 06547; Yr 60: NRG; Yr 61: Cynthia L. Karlic; Yr 62: Regional Environmental Manager; Yr 65: P.O. Box 1001 1866 River Rd, Middletown CT 06547; Yr 69: Yes; Yr 80: Electric Utility; Yr 81: EGU; Yr 82: 4911; Yr 83: Electric Services; Yr 87: Combustion Engineering; Yr 88: Tangential fired; Yr 90: Combustion Engineering Tangential Fired; MW 92: 400; MMBtu/hr 94: 4684; MMBtu/hr 95: General Electric Steam Turbine; MWe 96: 400; MWe 97: at 90ºF; MWe 98: 402; MWe 99: at 20ºF; yrs 105: (0.3%) No. 6 oil; No. 2 for ignition only;; yrs 106: No. 6 No. 2; yrs 107: No. 6 oil; yrs 114: 0.25; yrs 115: No. 2 oil; yrs 116: for ignition only (per operator); yrs 122: 0.2; yrs 129: AEL of 0.15 non-ozone season average regardless of fuels burned; MMBtu/hr 132: 4684; lb/MMBtu 136: 0.28; lb/MMBtu 138: NA; ppmvd 140: FLER (max) per NRG report; lbs/MMBtu 141: 0.25; ppmvd 143: Primary fuel (No. 6 residual oil) only.; lbs/MMBtu 147: 0.15; ppmvd 149: regardless of fuels burned; ppmvd 154: 2010; ppmvd 155: 12; hrs 156: 510; MMBtu 157: 955986; MWh 158: 59969; tons/yr 159: 90.5; tons/yr 160: 2009; tons/yr 161: 12; hrs 162: 143; MMBtu 163: 374322; MWh 164: 24512; tons/yr 165: 40.4; tons/yr 168: None; tons/yr 173: 2010; hr 174: 374.2; hr 175: 353.5; hr 176: 22.3; hr 177: 375.8; hr 178: less -136 hrs than EPA-CAIROS report; MMBtu/yr 180: 799820; MMBtu/yr 181: less -16% MMBtu/hr than EPA-CAIROS report; MMBtu/yr 182: 61084; MMBtu/yr 183: same as EPA-CAIROS report, within ±5%; MMBtu/yr 186: 1.7%; MMBtu/yr 187: 2009; hr 188: 113; hr 189: 57; hr 190: 55.9; hr 191: 112.9; hr 192: less -30 hrs than EPA-CAIROS report; MMBtu/yr 194: 315720; MMBtu/yr 195: less -16% MMBtu/hr than EPA-CAIROS report; MWh 196: 24575; MWh 197: same as EPA-CAIROS report, within ±5%; MWh 200: 0.7%; hrs 201: 243.6; hrs 202: 243.6; MMBtu/yr 206: 557770; MMBtu 207: 557770; MMBtu 208: 557770; lbs/MMBtu 211: 0.28; lbs/MMBtu 212: 0.28; tons/yr 214: 78.09; tons/yr 215: 78.09; tons/yr 216: 78.0878
8306-04 | NRG | MV5 |  | 1: 33; 2: 19; 3: NRG Energy, Inc; 4: NRG; 5: 8306; 6: Montville; 7: Montville 5; 8: Montville Station; 10: Montville-5; 11: MV5; 12: 5; 13: 546; 14: Utility Boiler; 15: 1; 16: 1; 17: 4; 18: 8306-04; 19: Single utility boiler; 20: Registration; 21: R-107-0017; 24: R-107-0017; 32: NOx RACT Compliance; 33: 22a-174-22(f) (CAIR); 47: Montville; 48: 107; 49: - / - / 107 / -; 50: Montville; 52: NRG Energy, Inc; 53: Montville Power, LLC (Owner/Operator); Yr 58: NRG Energy, Inc.; Yr 59: P.O. Box 1001, 1866 River Rd, Middletown CT 06547; Yr 60: NRG; Yr 61: Cynthia L. Karlic; Yr 62: Regional Environmental Manager; Yr 65: P.O. Box 1001 1866 River Rd, Middletown CT 06547; Yr 69: Yes; Yr 80: Electric Utility; Yr 81: EGU; Yr 82: 4911; Yr 83: Electric Services; Yr 87: Combustion Engineering; Yr 88: Tangential fired; Yr 90: Combustion Engineering Tangential Fired; MW 92: 81; MW 93: 488.5; MMBtu/hr 94: 995; MMBtu/hr 95: General Electric Steam Turbine; MWe 96: 81; MWe 97: at 90ºF; MWe 98: 81.6; MWe 99: at 20ºF; yrs 105: (0.3%) No. 6 oil; No. 2 for ignition only; Nat Gas; yrs 106: No. 6 Nat Gas; yrs 107: No. 6 oil; yrs 114: 0.25; yrs 115: Nat. Gas; yrs 122: 0.2; yrs 129: AEL of 0.15 non-ozone season average regardless of fuels burned; MMBtu/hr 132: 995; lb/MMBtu 136: 0.23; lb/MMBtu 138: 0.15; ppmvd 140: FLER (max) per NRG report; lbs/MMBtu 141: 0.25; ppmvd 143: Primary fuel (No. 6 residual oil) only. If gas-fired is used a 0.200 lbs/MMBtu should be considered.; lbs/MMBtu 147: 0.15; ppmvd 149: regardless of fuels burned; ppmvd 154: 2010; ppmvd 155: 12; hrs 156: 1052; MMBtu 157: 631690; MWh 158: 50747; tons/yr 159: 31.9; tons/yr 160: 2009; tons/yr 161: 12; hrs 162: 256; MMBtu 163: 163032; MWh 164: 13005; tons/yr 165: 11.2; tons/yr 168: None; tons/yr 173: 2010; hr 174: 936.9; hr 175: 840.9; hr 176: 96; hr 177: 936.9; hr 178: less -115 hrs than EPA-CAIROS report; MMBtu/yr 180: 554880; MMBtu/yr 181: less -12% MMBtu/hr than EPA-CAIROS report; MMBtu/yr 182: 49615; MMBtu/yr 183: same as EPA-CAIROS report, within ±5%; MMBtu/yr 186: 7%; MMBtu/yr 187: 2009; hr 188: 210.9; hr 189: 97.4; hr 190: 113.5; hr 191: 210.9; hr 192: less -45 hrs than EPA-CAIROS report; MMBtu/yr 194: 150580; MMBtu/yr 195: same as EPA-CAIROS report, within ±10%; MWh 196: 12974; MWh 197: same as EPA-CAIROS report, within ±5%; MWh 200: 1.8%; hrs 201: 573.9; hrs 202: 573.9; MMBtu/yr 206: 352730; MMBtu 207: 352730; MMBtu 208: 352730; lbs/MMBtu 211: 0.23; lbs/MMBtu 212: 0.23; tons/yr 214: 40.56; tons/yr 215: 40.56; tons/yr 216: 40.5639
8306-05 |  | MV6 |  | 1: 34; 2: 20; 4: NRG; 5: 8306; 6: Montville; 7: Montville 6; 8: Montville Station; 10: Montville-6; 11: MV6; 12: 6; 13: 546; 14: Utility Boiler; 15: 1; 16: 1; 17: 5; 18: 8306-05; 19: Single utility boiler; 20: Registration; 21: R-107-0020; 24: R-107-0020; 32: NOx RACT Compliance; 33: 22a-174-22(f) (CAIR); 47: Montville; 48: 107; 49: - / - / 107 / -; 50: Montville; 52: NRG Energy, Inc; 53: Montville Power, LLC (Owner/Operator); Yr 58: NRG Energy, Inc.; Yr 59: P.O. Box 1001, 1866 River Rd, Middletown CT 06547; Yr 60: NRG; Yr 61: Cynthia L. Karlic; Yr 62: Regional Environmental Manager; Yr 65: P.O. Box 1001 1866 River Rd, Middletown CT 06547; Yr 69: Yes; Yr 80: Electric Utility; Yr 81: EGU; Yr 82: 4911; Yr 83: Electric Services; Yr 87: Combustion Engineering; Yr 88: Tangential fired; Yr 90: Combustion Engineering Tangential Fired No. 6 Oil; MW 92: 402; MMBtu/hr 94: 4658; MMBtu/hr 95: General Electric Steam Turbine; MWe 96: 407.4; MWe 97: at 90ºF; MWe 98: 409.9; MWe 99: at 20ºF; yrs 105: (0.3%) No. 6 oil; No. 2 for ignition only;; yrs 106: No. 6 No. 2; yrs 107: No. 6 oil; yrs 114: 0.25; yrs 115: No. 2 oil; yrs 116: for ignition only (per operator); yrs 122: 0.2; yrs 129: AEL of 0.15 non-ozone season average regardless of fuels burned; MMBtu/hr 132: 4658; lb/MMBtu 136: 0.27; lb/MMBtu 138: NA; ppmvd 140: FLER (max) per NRG report; lbs/MMBtu 141: 0.25; ppmvd 143: Primary fuel (No. 6 residual oil) only.; lbs/MMBtu 147: 0.15; ppmvd 149: regardless of fuels burned; ppmvd 154: 2010; ppmvd 155: 12; hrs 156: 426; MMBtu 157: 674427; MWh 158: 45724; tons/yr 159: 52.1; tons/yr 160: 2009; tons/yr 161: 12; hrs 162: 173; MMBtu 163: 325660; MWh 164: 21297; tons/yr 165: 33.4; tons/yr 168: None; tons/yr 173: 2010; hr 174: 338.5; hr 175: 316.2; hr 176: 22.3; hr 177: 338.5; hr 178: less -88 hrs than EPA-CAIROS report; MMBtu/yr 180: 630340; MMBtu/yr 181: same as EPA-CAIROS report, within ±10%; MMBtu/yr 182: 45753; MMBtu/yr 183: same as EPA-CAIROS report, within ±5%; MMBtu/yr 186: 1.3%; MMBtu/yr 187: 2009; hr 188: 123.8; hr 189: 102; hr 190: 21.9; hr 191: 123.9; hr 192: less -49 hrs than EPA-CAIROS report; MMBtu/yr 194: 265730; MMBtu/yr 195: less -18% MMBtu/hr than EPA-CAIROS report; MWh 196: 20976; MWh 197: same as EPA-CAIROS report, within ±5%; MWh 200: 0.6%; hrs 201: 231.15; hrs 202: 231.15; MMBtu/yr 206: 448035; MMBtu 207: 448035; MMBtu 208: 448035; lbs/MMBtu 211: 0.27; lbs/MMBtu 212: 0.27; tons/yr 214: 60.48; tons/yr 215: 60.48; tons/yr 216: 60.4847
8306-06 | NRG | NH1 |  | 1: 35; 2: 21; 3: NRG Energy, Inc; 4: NRG; 5: 8306; 6: Norwalk Harbor Station; 7: Norwalk Harbor Station 1; 8: Norwalk Harbor Station; 10: Norwalk Harbor-1; 11: NH1; 12: 1; 13: 548; 14: Utility Boiler; 15: 1; 16: 1; 17: 6; 18: 8306-06; 19: Single utility boiler; 20: Registration; 21: R-137-0028; 24: R-137-0028; 32: NOx RACT Compliance; 33: 22a-174-22(f) (CAIR); 47: Norwalk; 48: 137; 49: - / - / 137 / -; 50: Norwalk Harbor; 52: NRG Energy, Inc; 53: Norwalk Power, LLC (Owner/Operator); Yr 58: NRG Energy, Inc.; Yr 59: P.O. Box 1001, 1866 River Rd, Middletown CT 06547; Yr 60: NRG; Yr 61: Cynthia L. Karlic; Yr 62: Regional Environmental Manager; Yr 65: P.O. Box 1001 1866 River Rd, Middletown CT 06547; Yr 69: Yes; Yr 80: Electric Utility; Yr 81: EGU; Yr 82: 4911; Yr 83: Electric Services; Yr 87: Combustion Engineering; Yr 88: Tangential fired; Yr 90: Combustion Engineering Tangential Fired; MW 92: 164; MW 93: 353; MMBtu/hr 94: 1776; MMBtu/hr 95: General Electric Steam Turbine; MWe 96: 162; MWe 97: at 90ºF; MWe 98: 164; MWe 99: at 20ºF; yrs 105: (0.3%) No. 6 oil; No. 2 for ignition only;; yrs 106: No. 6 No. 2; yrs 107: No. 6 oil; yrs 114: 0.25; yrs 115: No. 2 oil; yrs 116: for ignition only (per operator); yrs 122: 0.2; MMBtu/hr 132: 1776; lb/MMBtu 136: 0.21; lb/MMBtu 138: NA; ppmvd 140: FLER (max) per NRG report; lbs/MMBtu 141: 0.25; ppmvd 143: Primary fuel (No. 6 residual oil) only. If gas-fired is used a 0.200 lbs/MMBtu should be considered.; lbs/MMBtu 147: 0.15; ppmvd 149: regardless of fuels burned; ppmvd 154: 2010; ppmvd 155: 12; hrs 156: 885; MMBtu 157: 447264; MWh 158: 38314; tons/yr 159: 36.4; tons/yr 160: 2009; tons/yr 161: 12; hrs 162: 304; MMBtu 163: 201785; MWh 164: 16636; tons/yr 165: 17.4; tons/yr 168: None; tons/yr 173: 2010; hr 174: 643.8; hr 175: 550.4; hr 176: 93.4; hr 177: 643.8; hr 178: less -241 hrs than EPA-CAIROS report; MMBtu/yr 180: 425640; MMBtu/yr 181: same as EPA-CAIROS report, within ±10%; MMBtu/yr 182: 38486; MMBtu/yr 183: same as EPA-CAIROS report, within ±5%; MMBtu/yr 186: 2.7%; MMBtu/yr 187: 2009; hr 188: 193.1; hr 189: 131; hr 190: 62.1; hr 191: 193.1; hr 192: less -111 hrs than EPA-CAIROS report; MMBtu/yr 194: 173890; MMBtu/yr 195: less -14% MMBtu/hr than EPA-CAIROS report; MWh 196: 16727; MWh 197: same as EPA-CAIROS report, within ±5%; MWh 200: 1.2%; hrs 201: 418.45; hrs 202: 418.45; MMBtu/yr 206: 299765; MMBtu 207: 299765; MMBtu 208: 299765; lbs/MMBtu 211: 0.21; lbs/MMBtu 212: 0.21; tons/yr 214: 31.48; tons/yr 215: 31.48; tons/yr 216: 31.4753
8306-07 |  | NH2 |  | 1: 36; 2: 22; 4: NRG; 5: 8306; 6: Norwalk Harbor Station; 7: Norwalk Harbor Station 2; 8: Norwalk Harbor Station; 10: Norwalk Harbor-2; 11: NH2; 12: 2; 13: 548; 14: Utility Boiler; 15: 1; 16: 1; 17: 7; 18: 8306-07; 19: Single utility boiler; 20: Registration; 21: R-137-0030; 24: R-137-0030; 32: NOx RACT Compliance; 33: 22a-174-22(f) (CAIR); 47: Norwalk; 48: 137; 49: - / - / 137 / -; 50: Norwalk Harbor; 52: NRG Energy, Inc; 53: Norwalk Power, LLC (Owner/Operator); Yr 58: NRG Energy, Inc.; Yr 59: P.O. Box 1001, 1866 River Rd, Middletown CT 06547; Yr 60: NRG; Yr 61: Cynthia L. Karlic; Yr 62: Regional Environmental Manager; Yr 65: P.O. Box 1001 1866 River Rd, Middletown CT 06547; Yr 69: Yes; Yr 80: Electric Utility; Yr 81: EGU; Yr 82: 4911; Yr 83: Electric Services; Yr 87: Combustion Engineering; Yr 88: Tangential fired; Yr 90: Combustion Engineering Tangential Fired; MW 92: 172; MMBtu/hr 94: 1776; MMBtu/hr 95: General Electric Steam Turbine; MWe 96: 168; MWe 97: at 90ºF; MWe 98: 172; MWe 99: at 20ºF; yrs 105: (0.3%) No. 6 oil; No. 2 for ignition only;; yrs 106: No. 6 No. 2; yrs 107: No. 6 oil; yrs 114: 0.25; yrs 115: No. 2 oil; yrs 116: for ignition only (per operator); yrs 122: 0.2; MMBtu/hr 132: 1776; lb/MMBtu 136: 0.21; lb/MMBtu 138: NA; ppmvd 140: FLER (max) per NRG report; lbs/MMBtu 141: 0.25; ppmvd 143: Primary fuel (No. 6 residual oil) only. If other oil-fired is used a 0.200 lbs/MMBtu should be considered.; lbs/MMBtu 147: 0.15; ppmvd 149: regardless of fuels burned; ppmvd 154: 2010; ppmvd 155: 12; hrs 156: 928; MMBtu 157: 533193; MWh 158: 45429; tons/yr 159: 43.9; tons/yr 160: 2009; tons/yr 161: 12; hrs 162: 458; MMBtu 163: 292868; MWh 164: 23327; tons/yr 165: 22.7; tons/yr 168: None; tons/yr 173: 2010; hr 174: 730.6; hr 175: 571.1; hr 176: 159.5; hr 177: 730.6; hr 178: less -197 hrs than EPA-CAIROS report; MMBtu/yr 180: 495170; MMBtu/yr 181: same as EPA-CAIROS report, within ±10%; MMBtu/yr 182: 45082; MMBtu/yr 183: same as EPA-CAIROS report, within ±5%; MMBtu/yr 186: 3.1%; MMBtu/yr 187: 2009; hr 188: 400.1; hr 189: 166.6; hr 190: 233.5; hr 191: 400.1; hr 192: less -58 hrs than EPA-CAIROS report; MMBtu/yr 194: 245080; MMBtu/yr 195: less -16% MMBtu/hr than EPA-CAIROS report; MWh 196: 23164; MWh 197: same as EPA-CAIROS report, within ±5%; MWh 200: 1.6%; hrs 201: 565.35; hrs 202: 565.35; MMBtu/yr 206: 370125; MMBtu 207: 370125; MMBtu 208: 370125; lbs/MMBtu 211: 0.21; lbs/MMBtu 212: 0.21; tons/yr 214: 38.86; tons/yr 215: 38.86; tons/yr 216: 38.8631
8305-01 | PSEG | NHB1 |  | 1: 37; 2: 23; 3: PSEG Power LLC, PSEG Fossil LLC, PSEG Power Connecticut; 4: PSEG; 5: 8305; 6: New Haven Harbor; 7: New Haven Harbor 1; 10: New Haven Harbor Station (NHHS) - Auxiliary Boiler; 11: NHB1; 12: NHB1; 13: 6156; 14: Utility Boiler; 15: 1; 16: 1; 17: 1; 18: 8305-01; 19: Single utility boiler; 21: CP/OP No. 117-0031; 23: 2014-12-08; 26: 117-001-TIV; 29: 117-0265-TV; 30: 2009-12-08; 34: 2010-04-30; 36: 2011-01-25; 37: 2011-01-27; 40: 8243; 44: 1922-07-26; 47: New Haven; 48: 117; 49: - / - / 117 / -; 50: New Haven Harbor Station (NHHS); 51: 1 Waterfront Street New Haven, CT 06512; 52: PSEG Power LLC; 53: PSEG (Owner/Operator); Yr 58: PSEG Fossil LLC; Yr 60: PSEG; Yr 61: Michael Stagliola; Yr 62: Plant Manager, New England Stations; Yr 63: Robert Silvestri; Yr 66: (203) 551-6032; Yr 69: Yes; Yr 70: PSEG Fossil LLC; Yr 75: 2011-01-25; Yr 80: Electric Utility; Yr 81: EGU; Yr 82: 4911; Yr 83: Electric Services; Yr 84: unit is not used to produce power for sale, ratherto provide auxiliarey steam for station use; Yr 85: burning residual fuel and/or No. 2 oil and uses propane ignitors; Yr 87: Not Known; MW 92: Unit is a steam boiler, only; year 101: 1975; year 102: 1975-01-01; yrs 103: 51.5949; yrs 106: propane (NG) at startup # 6 oil, max Sulfur 0.3% wdb (yielded NOx in excess) # 2 oil, max Sulfur 0.3% wdb; yrs 107: No. 6 oil; yrs 131: Stack Test; MMBtu/hr 132: 143.4; lbs/MMBtu 133: 0.4; ppmvd 135: per TA&O; lb/MMBtu 136: 0.4; lbs/MMBtu 141: 0.25; ppmvd 150: 2010-02-03; ppmvd 151: 2015-02-03; ppmvd 152: 4.9993; ppmvd 154: 2010; ppmvd 155: 12; hrs 156: 1077; MMBtu 157: 1842328; MWh 158: 168256; tons/yr 159: 127.5; tons/yr 160: 2009; tons/yr 161: 12; hrs 162: 703; MMBtu 163: 1640110; MWh 164: 152988; tons/yr 165: 115.4; tons/yr 166: year-round (providing aux. steam to NHHS); tons/yr 168: None; tons/yr 172: fuel flow; lbs/MMBtu 210: 0.4; lbs/MMBtu 211: 0.4; lbs/MMBtu 212: 0.4
8305-02 |  | BHB2 |  | 1: 38; 2: 24; 4: PSEG; 5: 8305; 6: Bridgeport Harbor Station; 7: Bridgeport Harbor Station 2; 10: Bridgeport Harbor Station (BHS) Unit No. 2; 11: BHB2; 12: BHB2; 13: 568; 14: Utility Boiler; 15: 1; 16: 1; 17: 2; 18: 8305-02; 19: Single utility boiler; 20: Registration; 21: R-0162; 23: 2012-02-02; 26: 15-TIV-001; 29: 015-0217-TV; 30: 2009-09-16; 40: 8242 8253; 44: 8242 8253; 47: Bridgeport; 48: 15; 49: - / - / 015 / -; 50: Bridgeport Harbor Station (BHS); 51: 1 Atlantic Street, Bridgeport, CT 06604; 52: PSEG Power LLC; 53: PSEG Power Connecticut, LLC (Owner/Operator); Yr 58: PSEG Fossil LLC; Yr 60: PSEG; Yr 69: Yes; Yr 80: Electric Utility; Yr 81: EGU; Yr 82: 4911; Yr 83: Electric Services; Yr 84: TAO# 8242 - for CERC TAO# 8253 - for DERC; Yr 85: burning residual oil and using #2 oil at startup; Yr 87: Babcock and Wilcox; Yr 90: residual oil-fired cyclone unit; MW 92: 170; MW 93: 602; month 100: Aug; year 101: 1961; year 102: 1961-01-01; yrs 103: 65.5935; yrs 106: # 2 at startup residual oil; yrs 107: No. 6 oil; yrs 115: No. 2 oil; MMBtu/hr 132: 1785; lbs/MMBtu 141: 0.15; ppmvd 154: 2010; ppmvd 155: 12; hrs 156: 157; MMBtu 157: 105337; MWh 158: 8430; tons/yr 159: 14.8; tons/yr 160: 2009; tons/yr 161: 12; hrs 162: 161; MMBtu 163: 66280; MWh 164: 4917; tons/yr 165: 8.6; tons/yr 167: ESP for PM; tons/yr 168: None; tons/yr 172: CEMS for NOx, SO2 & CO2 COMS for opacity
8305-03 |  | BHB3 |  | 1: 39; 2: 25; 4: PSEG; 5: 8305; 6: Bridgeport Harbor Station; 7: Bridgeport Harbor Station 3; 10: Bridgeport Harbor Station (BHS) Unit No. 3; 11: BHB3; 12: BHB3; 13: 568; 14: Utility Boiler; 15: 1; 16: 1; 17: 3; 18: 8305-03; 19: Single utility boiler; 21: CP/OP No. 015-0089; 23: 2012-02-02; 26: 15-TIV-001; 29: 015-0217-TV; 30: 2009-09-16; 40: 8244; 44: 1922-07-27; 47: Bridgeport; 48: 15; 49: - / - / 015 / -; 50: Bridgeport Harbor Station (BHS); 51: 1 Atlantic Street, Bridgeport, CT 06604; 52: PSEG Power LLC; 53: PSEG Power Connecticut, LLC (Owner/Operator); Yr 58: PSEG Fossil LLC; Yr 60: PSEG; Yr 69: Yes; Yr 80: Electric Utility; Yr 81: EGU; Yr 82: 4911; Yr 83: Electric Services; Yr 84: in-line heater removes excess moisture from coal prior to combustion; Yr 85: installed in 1968, reconverted to coal in 1984, currently configured to coal and # 6 oil; Yr 87: Combustion Engineering; Yr 90: tangentially fired dual-fuel boiler with in-line heater and dense pack turbine; MW 92: 410; month 100: Aug; year 101: 1968; year 102: 1968-08-01; yrs 103: 58.0124; yrs 106: # 2 or #6 at startup coal (in boiler) and coal & #6 (in in-line heater); yrs 107: Coal; yrs 115: No. 6 oil; yrs 123: No. 2 oil; MMBtu/hr 132: 4100; lbs/MMBtu 141: 0.38; ppmvd 154: 2010; ppmvd 155: 12; hrs 156: 4583; MMBtu 157: 13168116; MWh 158: 1302618; tons/yr 159: 934.1; tons/yr 160: 2009; tons/yr 161: 12; hrs 162: 3767; MMBtu 163: 11147747; MWh 164: 1070682; tons/yr 165: 838.2; tons/yr 167: ESP & Pulse-jet fabric filer bagouse (coal only) for PM Activated Carbon Injection (coal only) - for Hg, LNB for NOx; tons/yr 168: None; tons/yr 172: CEMS for NOx, SO2 & CO2 COMS for opacity
Note: Facility Name above is used to retrieve data from EPA CAIROS

## 13(an)
[8 empty] | Summary: | [280 empty] | WTC | 6.174
[8 empty] | – | Table below includes cost analysis data entries and controls cost effectiveness assessment | [244 empty] | 20 | [51 empty] | 25
[8 empty] | – | Emission units general specifications - in Col. 1 through 24 | [210 empty] | DC Fctr | IC Fctr | Contingency Fctrs |  |  | Pre-Prod Fctr | Inv Fctr | Overhead | Profit | [24 empty] | TURBINES | 7% | [34 empty] | CFI 1990 | 1.73 | [14 empty] | TURBINES | 7%
[8 empty] | – | Uncontrolled NOx assessment - Col. 25 - 43; NOx Controls Proposed - Col 44-50, and Controlled NOx Assessment - Col. 51-87 | [207 empty] | Tax Factor x PrC |  |  | 1 | 2 | 3 | 4 |  | 5 | 6 | 7 | 8 | [25 empty] | 0.094393 | [31 empty] | CT-kW/H | 50 |  | CFI 1993 | 1.57 | [15 empty] | 0.085811
[8 empty] | – | Section I - Total Capital Cost Per Stakeholder's Report - Col 88-206 | [206 empty] | Std - 1 | 6% |  | Std - 1 | 45% | 33% |  | 20% | [30 empty] | 40 | [31 empty] | CT-kWh Cost | 388.16 |  | M | 1.3 |  |  |  | Labor Rate | Replacement Parts | [10 empty] | 40
[8 empty] | – | Section II - Total Capital Cost Analysis Corrected (Based On Reported Eq_Cost And Assigned Multipliers For Direct, Indirect & Contingency Costs) - Col. 207-256 | [203 empty] | 1 | 2 | 3 | Prog - 2 | 6% |  | Prog - 2 | 45% | 20% |  | 15% |  | 2% | 0% | [16 empty] | 30% M | 4%EC | [8 empty] | BOILERS | 7% | [29 empty] | LHV | WFR | UB-kW/H | 200 | Ammonia | Steam | Catalyst Disposal Fee |  |  | WI | 60.64 | 1.5% |  | M | [7 empty] | BOILERS | 7%
[8 empty] | – | Section III- TCC & Annual Costs Assessed Based On EPA Documents - Leveled Cost Analysis, Col 257-305 | [203 empty] | 1 | HPWI | 5% | Alt - 3 | 0% |  | Alt - 3 | 0% | 0% | 8% | 10% |  |  |  | 5% | 5% | [14 empty] | 30% | 4% | [9 empty] | 0.075009 | [27 empty] | 7% |  | 18330 | 0.7 |  | 212.22 | 360 | 6 | 15 |  |  |  | 50% Full Time | 4000 |  | 290 | [8 empty] | 0.075009
x
[254 empty] | COL II | [7 empty] | COL II
[74 empty] | Formulas to be used for verification only | [11 empty] | Formulas to be used for verification only
[74 empty] | AM |  |  | AP | AP | AN | [6 empty] | AS | AV | AV | AT | [142 empty] | COL II |  | COL II
[74 empty] | Heat Input per unit |  |  | NOx (UC) per unit | NOx (UC) per unit | NOx Rate | [6 empty] | Heat Input per unit | NOx (UC) per unit | NOx (UC) per unit | NOx Rate
[73 empty] | 8 CHKS | [11 empty] | 8 CHKS | [122 empty] | COL I |  |  | COL I
[73 empty] | 10 CHKS | [10 empty] | for SCR only, if η is given | 10 CHKS | [109 empty] | for Turbines, Diesel Eng | for Utility Boilers
#VALUE!
[44 empty] | CRRA 1st row only | [196 empty] | Annual Indirect Cost Fctr
[95 empty] | Notes: | [157 empty] | Capital Recovery (CR) Code | [16 empty] | http://www.bls.gov/data/inflation_calculator.htm | [6 empty] | Annual Direct Cost Code
[8 empty] | NOx CONTROL OPTIONS COST ANALYSIS | [86 empty] | If not reported Eqp Cost = TCC | [40 empty] | Gen Facility | Eng | Process Contingcy | [8 empty] | Contingency | Pre_prod | [45 empty] | (M) |  |  | Plant Overhead | G&A Taxes | [54 empty] | 1 | Combustion Turbines & Diesel Engines | [15 empty] | Base Year | 1990 | [5 empty] | 1 | HPWI, ULSF, Nat Gas | [22 empty] | Note: |  | 60% | 4%
[21 empty] | Table 8 | [73 empty] | If not reported Primary Control Cost = Eqp Cost | [40 empty] | 5% | 10% | 5% | [8 empty] | 15% | 2% | [48 empty] | 30% | 4% | [54 empty] | 2 | Utility Boilers | [15 empty] | CFI | 1.73 | [5 empty] | 2 | SCR, New Equipment | [22 empty] | B3 = $0
[7 empty] | GENERAL SPECIFICATIONS | [23 empty] | UNCONTROLLED NOx ASSESSMENT | [18 empty] | NOx CONTROL OPTION PROPOSED | [6 empty] | CONTROLLED NOx ASSESSMENT | [34 empty] | NOx CONTROL EQUIPMENT |  | SECTION I - TOTAL CAPITAL COST PER OWNERS' REPORT | [115 empty] | NOx CONTROL - (CE) COST EFFECTIVENESS per STK REPORT DATA |  |  | SECTION II - TOTAL CAPITAL COST ANALYSIS CORRECTED (based on reported eq_cost and assigned multipliers for direct, indirect & contingency costs) | [46 empty] | (CE) NOx CONTROL COST EFFECTIVENESS at CORRECTED STK REPORT DATA |  |  | SECTION III - TCC & ANNUAL COSTS ASSESSED BASED ON EPA ACT - LEVELED COST ANALYSIS | [45 empty] | (CE) NOx CONTROL COST EFFECTIVENESS at EPA ACT DATA
[7 empty] | REGISTRATION & ID | [7 empty] | FACILITY & EMISSION UNIT SPECIFICATIONS | [11 empty] | NOx EMISSION RATES |  |  |  | OPERATION REFERENCE # 1 | [5 empty] | OPERATION REFERENCE # 2 | [6 empty] | OPERATION REFERENCE # 3 | [5 empty] | NOx Control Option Seq. | ID | Option No. | NOx Control Type | NOx Control Basic /Generic Type | Cost Analysis Method: 1 - Std 2 - Prog 3 - Custom | Notes | Operation Time Period Reference No. 1 | Notes | NOx (C) - Controlled NOx - Ref 1 | [8 empty] | Operation Time Period Reference No. 2 (Stk Report) | Notes | NOx (C) - Controlled NOx - Ref 2 | [10 empty] | Operation Time Period Reference No. 3 (CAIR OS - max within last 3 yrs) | Notes | Control Option ID | NOx (C) - Controlled NOx - Ref 3 | [7 empty] | Type | Notes | TOTAL CAPITAL COST REPORTED BY STK | Equipment Capital Costs Reported - per group of identical units | [60 empty] | CUMMULATIVE EQUIPMENT CAPITAL COSTS PER UNIT | [19 empty] | DIRECT + INDIRECT + CONTINGENCY + CAPITAL COSTS PER UNIT | [11 empty] | ANNUAL COSTS | [21 empty] | (CE) Ref 1 (Stk Report) | (CE) Ref 2 (Stk Report) | (CE) Ref 3 (CAIR OS - max within last 3 yrs) | CLC IDX | EQIPMENT COST CORRECTED |  |  |  |  | EQUIPMENT COST PER MW NOM | DIRECT, INDIRECT & CONTINGENCY COSTS |  |  |  |  | SET-UP COSTS |  | OVERHEAD & PROFIT |  | TCC CORRECTED |  |  |  |  | TCC per unit per MW Nominal | Annual Costs (COL II) | [24 empty] | (CE) Ref 1 (Stk Report) | (CE) Ref 2 (Stk Report adj/clc) | (CE) Ref 3 (CAIR OS - max within last 3 yrs) | Units Specs |  | CORRECTED TCC PER STAKEHOLDER'S REPORTS - NO LOSS OF REVENUE ADJ |  |  |  |  | TCC ASSESSED (BASED ON EPA ACT & SELECTION) | [6 empty] | Annual Costs (COL III) | [31 empty] | (CE) Ref 1 (Stk Report) | (CE) Ref 2 (Stk Report adj) | (CE) Ref 3 (CAIR OS - max within last 3 yrs)
[7 empty] | No. | Seq | Stk No. | Owner/Operator | TAO | TA&O ID | Group Name | Unit Tag | No identical Units w/ same controls | Nom BTU/hr Capacity | Nom. Power Capacity | Facility Total Power Installed | Application Emmision Unit Type | Manufacturer | Model | Type | Date of Mfg or Installation | Age | Primary Fuel | Secondary Fuel | Stack Test Rate | Stack Test Rate | FLER | FLER | Operation Time Reference No. 1 (Stk Report) | NOx (UC) - Uncontrolled NOx - Ref 1 |  |  |  |  | Operation Time Reference No. 2 (Stk Report) | NOx (UC) - Uncontrolled NOx - Ref 2 | [5 empty] | Operation Time Reference No. 3 (CAIR OS - max within last 3 yrs) | NOx (UC) - Uncontrolled NOx - Ref 3 | [13 empty] | Controlled NOx Rate | Controlled NOx Rate | NOx(C) Assessed per Group Combined | NOx(C) Assessed Per Unit | NOx Estim Tons/yr (clc) | NOx (R) Reduced |  |  | Nom. Eff. |  |  | Controlled NOx Rate | Controlled NOx Rate | NOx(C) Assessed per Group Combined (per stk report) | NOx(C) Assessed Per Unit | NOx Estim Tons/yr (clc) | NOx (R) Reduced per Group Combined (provided by stk) | NOx (R) Reduced avg per unit (provided by stk) | NOx (R) Reduced per unit |  |  | Nom. Eff. |  |  |  | Controlled NOx Rate | Controlled NOx Rate | NOx Estim per unit Tons/yr (clc) | NOx (R) Reduced |  |  | Nom. Eff. | Nom. Eff.Override |  |  |  | CONTROL EQUIPMENT # 1 | [16 empty] | CONTROL EQUIPMENT # 2 AND OTHER COMBINATION OF TECHNOLOGIES CUMMULATIVE COSTS | [16 empty] | CUMULATIVE EQUIPMENT COST |  |  | DIRECT COST |  |  |  | INDIRECT COST | [7 empty] | CONTINGENCY |  |  |  | SET-UP COSTS |  | OVERHEAD & PROFIT |  | TOTAL CAPITAL COST (per whole group) |  |  |  | Equipment Cost Reported per Unit | PRIMARY CONTROLS COSTS |  | AUXILIARY EQUIPMENT |  | EQUIPMENT RETROFIT MODIFICATIONS |  | PRIMARY CONTROLS TOTAL COST |  | STRUCTURAL MAT"LS & MODIFICATION |  | EASEMENT MODFICATION |  | PERMITTING |  | PROCUREMENT COST | TAXES & FREIGHT |  | ESTM CHECK | EQUIPMENT COST PER MW NOM | DIRECT + INDIRECT COSTS |  |  |  |  | CONTINGENCY |  |  | TOTAL CAPITAL COST PER UNIT |  |  |  | ANNUAL COSTS - TOTALS PER GROUP | [12 empty] | ANNUAL COSTS - TOTALS PER UNIT | [12 empty] | PROCUREMENT COST | PERMITTING | EASEMENT MODIF. | TAXES & FREIGHT | EQUIP COST (re-clc) |  | DIRECT COST (re-clc) | INDIRECT COST (re-clc) | CONTINGENCY COST (re-clc) |  |  | (may be included in Owner's Cost) |  | OVERHEAD | PROFIT | TOTAL CAPITAL COST BEFORE ADJ | ADJUSTMENTS TO TOTAL CAPITAL COST |  | (TCC) Total Capital Cost per Unit | Remark |  | Project Management PM (% TCC add) | Project Management PM (add to TCC) | ANNUAL VARIABLE COSTS - TOTALS PER GROUP | [13 empty] | ANNUAL COSTS - TOTALS PER UNIT | [11 empty] | Nom Capacity | Type | Composite Controls TCC per stakeholder | NOx CONTROLS TCC |  |  |  | EPA ACT TCC |  | Controls Selected TCC |  |  |  | TCC Combined | Reference Data |  |  |  | SCR INPUT DATA |  |  | WATER INPUT DATA |  |  | Annual Direct per EPA Method | [12 empty] | Annual Direct Cost per Stk Data - REFERENCE ONLY |  |  | Annual Indirect Cost |  |  |  |  | TOTAL ANNUAL COST
[32 empty] | Avg Op. Time/yr | Heat Input | NOx Rate | NOx Rate | NOx (UC) avg per unit |  | Avg Op. Time/yr | Heat Input per group | Heat Input Avg per Unit | NOx Rate | NOx Rate | NOx (UC) avg per unit |  | Avg Op. Time/yr-unit | Heat Input per unit (max within a group) | NOx Rate (re-clc as 2000 NOx/HI) | NOx Rate (re-clc as 2000 NOx/HI) | NOx (UC) per unit (max within a group) | [45 empty] | Equipment #1 Cost reported by stk | EQUIPMENT PROCUREMENT COSTS |  |  |  |  | DIRECT COSTS INCLUDED IN EQP COST |  |  |  |  | INDIRECT COSTS INCLUDED IN EQP COST |  |  |  | PROCUREMENT COST | Taxes & Freight | Equipment #2 Cost reported by stk | EQUIPMENT PROCUREMENT COSTS |  |  |  |  | DIRECT COSTS INCLUDED IN EQP COST |  |  |  |  | INDIRECT COSTS INCLUDED IN EQP COST |  |  |  | PROCUREMENT COST | Taxes & Freight | Cumulative Equipment Cost | Estm Multiplier (per EPA Act ± 30%) | Eqp Cost Assessed | Building(s) Furnish and Erect Contracts | Construction Contracts Installation Cost | (Factored) Direct Installation Cost | Total Direct Cost | Indirect Costs Estm |  |  | (Factored) Indirect Installation Cost | Services & Testing Contracts | Engineering Contractor Direct Costs Contractor Agreements | Owner's Costs Start-up Permits | Total Indirect Cost | Estm Contingency Ec, Site, Project | Constr. Contingency | CONT. factored if reported) | TOTAL CONTINGENCY | (may be included in Owner's Cost) |  | OVERHEAD | PROFIT | TOTAL CAPITAL COST BEFORE ADJ | ADJUSTMENTS TO TOTAL CAPITAL COST |  | TCC Reported Total per whole group of identical units |  | (Eqp # 1 + Eqp #2) |  | (Aux Eqpt, El, Control Acc, Piping) |  | (Existing Units Retrofit Costs) |  | (aux eqp + eqp retrofit cost, included) |  | Foundations, Support Mat's & other Costr Contracts included in Eqp Cost |  | (included in Eqp cost, but usually is in Direct Cost) |  | (air permits + other included in Eqp cost, usually in Owner Costs) |  | (no Easement Mod & Permits) |  |  |  |  | DIRECT COST |  | INDIRECT COST |  |  | Contingency | Contingency % vs Equip Cost | Contingency % vs Composite Cost (EqC+DC+IC) | TCC - per unit | Total Capital Cost per Unit (clc chck) | Diff TCC % calculated vs. reported | TCC per unit per MW Nominal | STK REPORTED ANNUAL COSTS |  |  |  | Project Management PM (% TCC add) | Project Management PM (add to TCC) | ANNUAL VARIABLE COST - per group |  |  | PLANT OVERHEAD 30% (M) | G&A TAX, INSURANCE (4% Eqp C) | CAPITAL RECOVERY (as shown in stk report) | TOTAL ANNUAL COST (per report) | ANNUAL VARIABLE COST - per unit |  |  | PLANT OVERHEAD 30% (M) | G&A TAX, INSURANCE (4% Eqp C) | CAPITAL RECOVERY (as shown in stk report) | TOTAL ANNUAL COST (clc) | Total Annual Cost Verification | [13 empty] | TAXES & CONT FACTORS | CONSTR. CONT | TOTAL CONTINGENCY | Pre-production Cost | Inventory Capital |  |  |  | EXISTING EQUIPMENT SALVAGE VALUE | LOST REVENUES | [5 empty] | DIRECT ANNUAL COST - per group |  |  |  |  | INDIRECT ANNUAL COSTS |  |  |  | TOTAL DIRECT INDIRECT COST | TOTAL DIRECT COST PER UNIT |  | TOTAL INDIRECT PER UNIT |  | TOTAL DIRECT & INDIRECT COST (per unit) | Total Dirct/Indirect vs. Total Annual | CR Code | CAPITAL RECOVERY | TOTAL ANNUAL COST | Total Annual Cost Verification | [9 empty] | 1st Control TCC | 2nd Control TCC | 3rd Control TCC | 4th Control TCC | EPA ACT Cost (1990) | EPA ACT Cost (2011) | 1st Control TCC | 2nd Control TCC | 3rd Control TCC | 4th Control TCC |  | Control Code | H | HI | NOx(R) | Y | CRF | V | F | W | GPM | A2.1 | A2.2 | A2.3 | A3.1 | A4.1 | A4.2 | A | B1 | B2 | M=B1+B2 | B3 | B | Total Annual Direct Cost | A | B = B1+B2 | Total Annual Direct Cost | 1 | 2 | 3 |  | C
[96 empty] | Primary Control System Cost or Retrofit Cost | Auxiliary Equipment | Aux. Electrical Instrumentation | Control System Accesories (PLC, DCS) | Control Software + License fees | Piping, Ftgs, Ductwork, Insulation | Existing Equipment Modifications | Structural Mat'ls & Modifications Foundations & Support | Other Construction Costs | Easement Modif. | Engineering | Service, Testing, Modelling Contracts | Permitting | Other Permits | Total Eqp Cost subject to Taxes & Freight (no Easement Mod & Permits |  |  | Primary Control System Cost or Retrofit Cost | Auxiliary Equipment | Aux. Electrical Instrumentation | Control System Accesories (PLC, DSC) | Control Software + License fees | Piping, Ftgs, Insulation | Existing Equipment Modifications | Structural Mat'ls & Modifications Foundations & Support | Other Construction Costs | Easement Modif. | Engineering | Service, Testing, Modelling Contracts | Permitting | Other Permits | Total Eqp Cost subject to Taxes & Freight (no Easement Mod & Permits | [8 empty] | Indirect Cost - Gen Facilities | Indirect Cost - Eng & Office | Indirect Cost - Process Contingency | [9 empty] | Pre-production Cost | Inventory Capital |  |  |  | EXISTING EQUIPMENT SALVAGE VALUE | LOST REVENUES |  |  | Primary Control(s) (Cumulative Cost) per unit | PrC % Eqp Cst | Aux Eqpt+Acc El + Control Syst Mod | Aux Eqp % Pr C | Primary Units Retrofit (RC) Cumulative Cost per unit | RC % Eqp Cst | Primary Control Cost | Eqp DC % Eqp C | Cummulative Sructural Mod costs per unit | % | Easement Modification Cost | % | Cum Permitting Costs per unit | % | Total Eqp Cost subject to Taxes & Freight | Taxes & Freight | Taxes & Freight % |  |  | Direct Inst. Cost | Direct Cost % vs Equip Cost | Indirect Cost | Indirect Cost % vs Equip Cost | Indirect Cost % vs Composite Cost (EqC+DC) | [7 empty] | TOTAL ANNUAL COST (per report) | COST EFF (per report) | NOx (R) - per group (if none enter 1 ton) | COST EFF Chck (per report) |  |  | (Added) Maintenance Cost | Total Variable Costs | TOTAL DIRECT ANNUAL COST |  |  |  |  | (Added) Maintenance Cost | Total Variable Costs | TOTAL DIRECT ANNUAL COST |  |  |  |  | TOTAL ANNUAL COST (per report) | Total Annual Cost Deviation % | [27 empty] | (M) Added Maintenance (included in OP) | (M) per hrs of Operation | Total Variable Costs (TVC) | TVC / MMBtu Heat Input | TOTAL DIRECT ANNUAL COST | ANL IC Fctr | PLANT OVERHEAD 30% (M) | G&A TAX, INSURANCE (4% Eqp C) | TOTAL INDIRECT ANNUAL COST |  | Total Direct Cost | Total Direct % Total Annual | Total Indirect Cost | Total Indirect % Total Annual | [5 empty] | TOTAL ANNUAL COST (per report) | Total Annual Cost Deviation % | Remark | Detail | [18 empty] | Avg op Time | Heat Input | NOx Removed | Catalyst Replacement Cycle | Catalyst CRF | Catalyst Volume | FUEL | WATER RATE | WATER GPM | Electricity | Ammonia | Steam | Water Supply Treatment (Catalyst) Disposal | Performance Loss | Blower | Total Variable | Semi-Variable Maintenance | Maintenance Parts | Maintenanace | Replacement Parts | Total Semi-Variable |  | Variable Cost | Semi-Variable Maintenance |  | Plant Overhead | G&A | CR Code | Capital Recovery | Total Annual Indirect Cost
[16 empty] | Btu/hr | MW | MW | [5 empty] | yrs |  |  | lb/MMBtu | ppmvd | lbs/MMBtu | ppmvd |  | hrs/yr | MMBtu | lbs/MMBtu | ppmvd | tons/yr |  | hrs/yr |  | MMBtu | lbs/MMBtu | ppmvd | tons/yr |  | hrs/yr | MMBtu | lbs/MMBtu | ppmvd | tons/yr | [9 empty] | lbs/MMBtu | ppmvd | tons/yr | tons/yr | tons/yr | tons/unit | % | % | % |  |  | lbs/MMBtu | ppmvd | tons/yr | tons/yr | tons/yr | tons/yr | tons/unit | tons/unit | % | % | % |  |  |  | lbs/MMBtu | ppmvd | tons/yr | tons/unit | % | % | % |  |  |  | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ |  |  |  | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | % | $ | % |  |  | $ | % | [6 empty] | $ | $ | % | % | $/MW | $ | % | $ | % |  | $ | % |  | $ | $ | % | $$/MW Nom | $ | $ | tons/yr |  | % | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | % | $/ton NOx(R) | $/ton NOx(R) | $/ton NOx(R) |  | $ | $ | $ | $ | $ |  | $ | $ |  |  | $ | $ | $ | $ | $ | $ | $ | $ | $ |  | $$/MW Nom | % | $ | $ | $/hr | $ |  | $ |  | $ | $ | $ | $ | $ | $ | $ | $ | $ |  |  | $ | $ | $ | % |  |  | $/ton NOx(R) | $/ton NOx(R) | $/ton NOx(R) | $ |  | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ |  | hrs/yr | MMBtu/yr | tons/yr | yrs |  | ft³ | lb/hr | lb/hr | gpm | $ | $ | $ | $ |  |  | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $ | $/ton NOx(R) | $/ton NOx(R) | $/ton NOx(R)
REFERENCE ID | [6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117 | 118 | 119 | 120 | 121 | 122 | 123 | 124 | 125 | 126 | 127 | 128 | 129 | 130 | 131 | 132 | 133 | 134 | 135 | 136 | 137 | 138 | 139 | 140 | 141 | 142 | 143 | 144 | 145 | 146 | 147 | 148 | 149 | 150 | 151 | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181 | 182 | 183 | 184 | 185 | 186 | 187 | 188 | 189 | 190 | 191 | 192 | 193 | 194 | 195 | 196 | 197 | 198 | 199 | 200 | 201 | 202 | 203 | 204 | 205 | 206 | 207 | 208 | 209 | 210 | 211 | 212 | 213 | 214 | 215 | 216 | 217 | 218 | 219 | 220 | 221 | 222 | 223 | 224 | 225 | 226 | 227 | 228 | 229 | 230 | 231 | 232 | 233 | 234 | 235 | 236 | 237 | 238 | 239 | 240 | 241 | 242 | 243 | 244 | 245 | 246 | 247 | 248 | 249 | 250 | 251 | 252 | 253 | 254 | 255 | 256 | 257 | 258 | 259 | 260 | 261 | 262 | 263 | 264 | 265 | 266 | 267 | 268 | 269 | 270 | 271 | 272 | 273 | 274 | 275 | 276 | 277 | 278 | 279 | 280 | 281 | 282 | 283 | 284 | 285 | 286 | 287 | 288 | 289 | 290 | 291 | 292 | 293 | 294 | 295 | 296 | 297 | 298 | 299 | 300 | 301 | 302 | 303 | 304 | 305
8298-01 | CDECCA | GT | 8298-01-01 |  | Nat Gas |  | 1: 1; 2: 1; 3: 1; 4: Capitol District Energy Center Cogeneration Associates; 5: 8298; 6: 8298-01; 7: Capitol District Energy Center; 8: GT; 9: 1; 13: Combustion Turbine; 14: General Electric; 15: PG 6531; 16: Cogeneration Turbine; 18: 38 yrs; 19: Natural Gas; 20: No. 2 oil; 38: CAIR-OS (max last 3 yrs); 39: 324; 40: 128717; 41: 0.11; 43: 7.2; 45: 8298-01-01; 46: 1; 48: Nat Gas; 49: 4 - Custom; 50: Unit Owner report not provided; 75: CAIR OS - max within last 3 yrs; 149: 0; 155: 0; 178: 0; 179: 0; 181: 0; 247: 1; 271: 1; 272: 324; 273: 128717; 274: 0; 278: 21673.4693; 279: 15171.4285; 280: 30.3104; 281: 6288.192; 284: 8181.7193; 287: 14469.9113; 288: 33989.9328; 290: 33989.9328; 292: 33989.9328; 293: 48459.8441; 294: 901019; 295: 81000; 296: 982019; 297: 20393.9597; 299: 1
8302-01 | CRRA | 11A | 8302-01-01 | Selective Catalytic Reduction (SCR) | SCR |  | 2 | 2 | 2 | Connecticut Resources Recovery Authority | 8302 | 8302-01 | South Meadow Station | 11A | 8 |  | 40 | 160 | Combustion Turbine | Pratt & Whitney | TP4-2(A9) LF | TP | 1970 | 57 yrs | Jet Fuel A (Kerosene K1) | No. 2 oil | 0.675 | 132.5 | 0.81 |  | 48 hrs/year operation | 48 |  |  |  |  | 2009 Operating Schedule |  |  |  | 0.7305 | 129.3684 |  | CAIR-OS (max last 3 yrs) | 19 | 3819 | 0.79 | 139.9056 | 1.5 |  | 8302-01-01 | 1 | Selective Catalytic Reduction (SCR) | SCR | 4 - Custom |  | 48 hrs/year operation | [9 empty] | approx. 60% | 2009 operation | [6 empty] | 9.207 | 1.1509 | 1.1509 |  |  | 0.9 | CAIR OS - max within last 3 yrs |  |  | 0.078555 | 13.9906 | 0.15 | 1.35 | 0.9 | 0.90056 | 0.9 |  | Selective Catalytic Reduction (SCR) |  | 18266776 | 4825520 | 2272880 | 626000 | 547200 | 158400 |  | 1008000 |  | 213040 | [6 empty] | 4825520 | [18 empty] | 4825520 | 1.3 | 6273176 | 160000 | 9000000 |  | 9160000 | [5 empty] | 920000 |  | 920000 |  |  |  | 1913600 |  |  |  |  | 18266776 |  |  | 18266776 | 784147 | 284110 | 0.36232 | 292450 | 0.37295 | 0 | 0 | 576560 | 0.73527 | 26630 | 0.03396 | 0 | 0 | 0 | 0 | 603190 |  |  | 0 | 19603.675 | 1145000 | 1.4602 | 115000 | 0.14666 |  | 239200 | 0.30504 |  | 2283347 | 2283347 | 0 | 57083.675 | 4467166.0704 | 485192.3613 | 9.207 | 0 | 0 | 0 | 167167 |  | 167167 |  |  | 4299999.0704 | 4467166.0704 | 20895.875 |  | 20895.875 |  |  | 537499.8838 | 558395.7588 | 558395.7588 | 0 |  | 485192.3613 | 413626.488 | 4 | 603190 | 0 | 0 |  | 603190 | 15079.75 | 1145000 | 115000 |  | 239200 | 239200 |  |  |  |  | 2102390 |  |  | 2102390 | stk added + 8% | 52559.75 |  |  | 167167 |  |  |  | 167167 | 0 | 0 | 0 |  | 167167 | 20895.875 | 0.095264 |  |  | 20895.875 | 0.095264 | 1 | 198450.7432 | 219346.6182 | 558395.7588 | 0.60718 | stk added + 61% |  |  | 190591.1747 | 162478.9764 | 20 | SCR | 2102390 | 2102390 | 0 | 0 |  | 1453000 | 2513690 | 2513690 |  |  |  | 2513690 | 2 | 19 | 3819 | 1.35 | 1263.1579 | 0.07 | 1489.1566 |  |  |  | 806.436 | 840.78 | 563.8172 | 2705.053 | 737.504 | 73.7504 | 5727.3406 | 1993.2368 | 179.1004 | 2172.3372 |  | 2172.3372 | 7899.6778 | 1145.7 | 16544.9046 | 17690.6046 | 1303.4023 | 100547.6 | 1 | 215701.039 | 317552.0414 | 325451.7192 |  | 282786.3314 | 241075.3475
8302-02 | 0 | 11B | 8302-01-02 | HPWI + Ultra Low Sulfur Fuel | HPWI |  | 1: 3; 2: 3; 4: 0; 6: 8302-02; 8: 11B; 9: 8; 13: Combustion Turbine; 14: Pratt & Whitney; 15: TP4-2(A9) LF; 16: TP; 17: 1970; 18: 57 yrs; 19: Jet Fuel A (Kerosene K1); 20: No. 2 oil; 21: 0.71; 22: 138.4; 23: 0.81; 35: 0.7305; 36: 129.3684; 39: 20; 40: 4575; 41: 0.74; 43: 1.7; 45: 8302-01-02; 46: 2; 47: HPWI + Ultra Low Sulfur Fuel; 48: HPWI; 49: 4 - Custom; 50: Water Injection w/ Low Sulfur Fuel Combination; 62: 2009 operation; 69: 8.184; 70: 1.023; 71: 1.023; 74: 0.75; 75: CAIR OS - max within last 3 yrs; 78: 0.19639; 79: 34.9764; 80: 0.375; 81: 1.125; 82: 0.75; 83: 0.75141; 84: 0.75; 86: HPWI + Ultra Low Sulfur Fuel; 88: 11953900; 89: 4149000; 90: 1154000; 91: 1280000; 93: 115000; 96: 1600000; 104: 4149000; 106: 100000; 107: 100000; 108: 0; 121: 100000; 123: 4249000; 124: 1; 125: 4249000; 126: 160000; 127: 6850000; 129: 7010000; 135: 240000; 137: 240000; 141: 454900; 146: 11953900; 149: 11953900; 150: 531125; 151: 156750; 152: 0.29513; 153: 174375; 154: 0.32831; 155: 200000; 156: 0.37656; 157: 531125; 158: 1; 159: 0; 160: 0; 161: 0; 162: 0; 163: 0; 164: 0; 165: 531125; 168: 0; 169: 13278.125; 170: 876250; 171: 1.6498; 172: 30000; 173: 0.056484; 175: 56862.5; 176: 0.10706; 178: 1494237.5; 179: 1494237.5; 180: 0; 181: 37355.9375; 182: 3017969.06; 183: 525243.3086; 184: 8.184; 185: 0.29792; 188: 204021; 190: 204021; 193: 2813948.06; 194: 3017969.06; 195: 25502.625; 197: 25502.625; 200: 351743.5075; 201: 377246.1325; 202: 377246.1325; 203: 0; 205: 525243.3086; 206: 335329.8956; 207: 4; 208: 531125; 209: 0; 210: 0; 212: 531125; 213: 13278.125; 214: 876250; 215: 30000; 217: 56862.5; 218: 56862.5; 223: 1494237.5; 226: 1494237.5; 227: same TCC; 228: 37355.9375; 231: 204021; 235: 204021; 236: 0; 237: 0; 238: 0; 240: 204021; 241: 25502.625; 242: 0.15312; 245: 25502.625; 246: 0.15312; 247: 1; 248: 141045.4494; 249: 166548.0744; 250: 377246.1325; 251: 0.55852; 252: stk added + 56%; 255: 162803.5918; 256: 148042.7328; 257: 20; 258: Combined; 259: 1494237.5; 260: 1481737.5; 261: 12500; 262: 0; 264: N/A; 266: 1725675; 267: 12500; 270: 1738175; 271: 1; 272: 19; 273: 3819; 274: 1.125; 278: 10965.6301; 279: 7675.9411; 280: 15.3355; 281: 368.752; 284: 242.7495; 287: 611.5015; 288: 1993.2368; 289: 123.845; 290: 2117.0818; 292: 2117.0818; 293: 2728.5833; 294: 26733; 295: 4750; 296: 31483; 297: 1270.2491; 298: 69527; 299: 1; 300: 149153.6958; 301: 219950.9448; 302: 222679.5281; 304: 217673.048; 305: 197937.3583
8302-03 | 0 | 12A | 8302-01-03 | High Pressure Water Injection (HPWI) | HPWI |  | 1: 4; 2: 4; 4: 0; 6: 8302-03; 8: 12A; 9: 8; 11: 40; 13: Combustion Turbine; 14: Pratt & Whitney; 15: TP4-2(A9) LF; 16: TP; 17: 1970; 18: 57 yrs; 19: Jet Fuel A (Kerosene K1); 20: No. 2 oil; 21: 0.744; 22: 124.8; 23: 0.81; 35: 0.7305; 36: 129.3684; 45: 8302-01-03; 46: 3; 47: High Pressure Water Injection (HPWI); 48: HPWI; 49: 4 - Custom; 62: 2009 operation; 69: 6.138; 70: 0.76725; 71: 0.76725; 74: 0.6; 75: CAIR OS - max within last 3 yrs; 78: 0.31422; 79: 55.9622; 80: 0.6; 81: 0.9; 82: 0.6; 83: 0.60226; 84: 0.6; 86: High Pressure Water Injection (HPWI); 88: 11853900; 89: 4149000; 90: 1154000; 91: 1280000; 93: 115000; 96: 1600000; 104: 4149000; 123: 4149000; 124: 1; 125: 4149000; 126: 160000; 127: 6850000; 129: 7010000; 135: 240000; 137: 240000; 141: 454900; 146: 11853900; 149: 11853900; 150: 518625; 151: 144250; 152: 0.27814; 153: 174375; 154: 0.33623; 155: 200000; 156: 0.38564; 157: 518625; 158: 1; 159: 0; 160: 0; 161: 0; 162: 0; 163: 0; 164: 0; 165: 518625; 168: 0; 169: 12965.625; 170: 876250; 171: 1.6896; 172: 30000; 173: 0.057845; 175: 56862.5; 176: 0.10964; 178: 1481737.5; 179: 1481737.5; 180: 0; 181: 37043.4375; 182: 2914981.06; 183: 474907.3086; 184: 6.138; 185: 0; 188: 124573; 190: 124573; 193: 2790408.06; 194: 2914981.06; 195: 15571.625; 197: 15571.625; 200: 348801.0075; 201: 364372.6325; 202: 364372.6325; 203: 0; 205: 474907.3086; 206: 404858.4806; 207: 4; 208: 518625; 209: 0; 210: 0; 212: 518625; 213: 12965.625; 214: 876250; 215: 30000; 217: 56862.5; 218: 56862.5; 223: 1481737.5; 226: 1481737.5; 227: same TCC; 228: 37043.4375; 231: 124573; 235: 124573; 236: 0; 237: 0; 238: 0; 240: 124573; 241: 15571.625; 242: 0.10018; 245: 15571.625; 246: 0.10018; 247: 1; 248: 139865.5378; 249: 155437.1628; 250: 364372.6325; 251: 0.57341; 252: stk added + 57%; 255: 202589.9809; 256: 172707.9587; 257: 20; 258: HPWI; 259: 1481737.5; 260: 1481737.5; 261: 0; 262: 0; 264: 997500; 265: 1725675; 266: 1725675; 270: 1725675; 271: 1; 272: 19; 273: 3819; 274: 0.9; 278: 10965.6301; 279: 7675.9411; 280: 15.3355; 281: 368.752; 284: 242.7495; 287: 611.5015; 288: 1993.2368; 289: 122.9543; 290: 2116.1911; 292: 2116.1911; 293: 2727.6926; 294: 26733; 295: 4750; 296: 31483; 297: 1269.7147; 298: 69027; 299: 1; 300: 148081.0643; 301: 218377.779; 302: 221105.4716; 304: 288179.1745; 305: 245672.7462
8302-04 | 0 | 12B |  |  |  |  | 1: 5; 2: 5; 4: 0; 6: 8302-04; 8: 12B; 9: 8; 13: Combustion Turbine; 14: Pratt & Whitney; 15: TP4-2(A9) LF; 16: TP; 17: 1970; 18: 57 yrs; 19: Jet Fuel A (Kerosene K1); 20: No. 2 oil; 21: 0.706; 22: 114.8; 23: 0.81; 35: 0.7305; 36: 129.3684
8302-05 | 0 | 13A |  |  |  |  | 1: 6; 2: 6; 4: 0; 6: 8302-05; 8: 13A; 9: 8; 11: 40; 13: Combustion Turbine; 14: Pratt & Whitney; 15: TP4-2(A9) LF; 16: TP; 17: 1970; 18: 57 yrs; 19: Jet Fuel A (Kerosene K1); 20: No. 2 oil; 21: 0.75; 22: 132.5; 23: 0.81; 35: 0.7305; 36: 129.3684
8302-06 | 0 | 13B |  |  |  |  | 1: 7; 2: 7; 4: 0; 6: 8302-06; 8: 13B; 9: 8; 13: Combustion Turbine; 14: Pratt & Whitney; 15: TP4-2(A9) LF; 16: TP; 17: 1970; 18: 57 yrs; 19: Jet Fuel A (Kerosene K1); 20: No. 2 oil; 21: 0.733; 22: 130.3; 23: 0.81; 35: 0.7305; 36: 129.3684
8302-07 | 0 | 14A |  |  |  |  | 1: 8; 2: 8; 4: 0; 6: 8302-07; 8: 14A; 9: 8; 11: 40; 13: Combustion Turbine; 14: Pratt & Whitney; 15: TP4-2(A9) LF; 16: TP; 17: 1970; 18: 57 yrs; 19: Jet Fuel A (Kerosene K1); 20: No. 2 oil; 21: 0.755; 22: 124; 23: 0.81; 35: 0.7305; 36: 129.3684
8302-08 | 0 | 14B |  |  |  |  | 1: 9; 2: 9; 4: 0; 6: 8302-08; 8: 14B; 9: 8; 13: Combustion Turbine; 14: Pratt & Whitney; 15: TP4-2(A9) LF; 16: TP; 17: 1970; 18: 57 yrs; 19: Jet Fuel A (Kerosene K1); 20: No. 2 oil; 21: 0.771; 22: 136.1; 23: 0.81; 35: 0.7305; 36: 129.3684
8303-01 | FirstLight | 10 | 8303-01-01 | SCR + HPWI + CO Catalyst + Dual Fuel | SCR |  | 10 | 10 | 3 | FirstLight Hydro Generating Company | 8303 | 8303-01 | Tunnel | 10 | 1 |  | 20 | 20 | Combustion Turbine | Pratt & Whitney | FT4-8 | FT | Jan 1969 | 58 yrs | Jet Fuel A (Kerosene K1) |  | 0.698 | 119.6 | 0.72 |  | 50 hrs/yr operation | 50 | [5 empty] | 50 | 12450 | 12450 | 0.736 | 186.7072 | 4.5816 | CAIR-OS (max last 3 yrs) | 20 | 4575 | 0.743 | 188.4829 | 1.7 |  | 8303-01-01 | 1 | SCR + HPWI + CO Catalyst + Dual Fuel | SCR | 4 - Custom | Natural Gas with Oil backup | 50 hrs/year operation |  |  | 5 | [9 empty] | 0.01971 | 5 | 0.12269 | 0.12269 | 0.12269 |  |  | 4.4589 | 0.97322 | 0.97322 | 0.97322 | CAIR OS - max within last 3 yrs |  |  | 0.019902 | 5.0476 | 0.045526 | 1.6545 | 0.97322 | 0.97321 | 0.97322 |  | SCR + HPWI + CO Catalyst + Dual Fuel |  | 6310000 | 5250000 | 2550000 | 700000 |  |  |  | 1000000 | 1000000 | [7 empty] | 5250000 |  | 700000 | 600000 | 100000 | [12 empty] | 700000 |  | 5950000 | 1 | 5950000 | [11 empty] | 0 | [8 empty] | 5950000 |  | 360000 | 6310000 | 5950000 | 3150000 | 0.52941 | 1800000 | 0.30252 | 1000000 | 0.16807 | 5950000 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5950000 |  |  | 0 | 297500 |  |  | 0 | 0 |  |  |  |  | 6310000 | 6310000 | 0 | 315500 | 848019 | 190292 | 4.4589 | 0.0005598 | [6 empty] | 252400 | 595619 | 848019 |  |  |  |  | 252400 | 595619 | 848019 | 848019 | 0 |  | 190292 | 512561.0409 | 4 | 5950000 | 0 | 0 |  | 5950000 | 297500 |  | 0 |  |  | 0 |  |  |  |  | 5950000 |  | 360000 | 6310000 | same TCC | 315500 | [7 empty] | 1 |  | 252400 | 252400 | 252400 |  |  | 252400 | 0.29763 | 252400 | 0.29763 | 1 | 595619.3614 | 848019.3614 | 848019 | -4.2622e-07 | -4.2622e-07 |  |  | 190185.5555 | 512561.2593 | 20 | Combined | 5950000 | 2550000 | 700000 | 200000 | 2500000 | N/A |  | 2513690 | 1725675 | 200000 | 2500000 | 6939365 | 2 | 20 | 4575 | 1.6545 | 1200 | 0.07 | 1489.1566 |  |  |  | 848.88 | 1030.4065 | 690.9785 | 2705.053 | 776.32 | 77.632 | 6129.27 | 4196.288 | 520.4524 | 4716.7404 |  | 4716.7404 | 10846.0104 | 1372.5 | 16603.5646 | 17976.0646 | 2830.0442 | 277574.6 | 1 | 595470.4998 | 875875.1441 | 886721.1544 |  | 198865.2181 | 535953.4608
|  |  | 8303-01-02 | SCR + HPWI + CO Catalyst | SCR |  | 1: 11; 33: #N/A; 45: 8303-01-02; 46: 2; 47: SCR + HPWI + CO Catalyst; 48: SCR; 49: 4 - Custom; 50: Primary fuel Oil - Kerosene K1; 54: 10; 64: 0.03942; 65: 10; 66: 0.24539; 67: 0.24539; 68: 0.24539; 71: 4.3362; 72: 0.94644; 73: 0.94644; 74: 0.94644; 78: 0.039804; 79: 10.0951; 80: 0.091052; 81: 1.6089; 82: 0.94644; 83: 0.94643; 84: 0.94644; 86: SCR + HPWI + CO Catalyst; 88: 3630000; 89: 2750000; 90: 2550000; 91: 200000; 104: 2750000; 106: 700000; 107: 600000; 108: 100000; 121: 700000; 123: 3450000; 124: 1; 125: 3450000; 137: 0; 146: 3450000; 148: 180000; 149: 3630000; 150: 3450000; 151: 3150000; 152: 0.91304; 153: 300000; 154: 0.086957; 155: 0; 156: 0; 157: 3450000; 158: 1; 159: 0; 160: 0; 161: 0; 162: 0; 163: 0; 164: 0; 165: 3450000; 168: 0; 169: 172500; 172: 0; 173: 0; 178: 3630000; 179: 3630000; 180: 0; 181: 181500; 182: 487846; 183: 112635; 184: 4.3362; 185: 0.0011528; 192: 145200; 193: 342646; 194: 487846; 199: 145200; 200: 342646; 201: 487846; 202: 487846; 203: 0; 205: 112635; 206: 303207.9968; 207: 4; 208: 3450000; 209: 0; 210: 0; 212: 3450000; 213: 172500; 215: 0; 218: 0; 223: 3450000; 225: 180000; 226: 3630000; 227: same TCC; 228: 181500; 236: 1; 238: 145200; 239: 145200; 240: 145200; 243: 145200; 244: 0.29763; 245: 145200; 246: 0.29763; 247: 1; 248: 342646.3204; 249: 487846.3204; 250: 487846; 251: -6.5686e-07; 252: -6.5686e-07; 255: 112505.2238; 256: 303208.196; 257: 20; 258: Combined; 259: 3450000; 260: 2550000; 261: 700000; 262: 200000; 264: N/A; 266: 2513690; 267: 1725675; 268: 200000; 270: 4439365; 271: 2; 272: 20; 273: 4575; 274: 1.6089; 275: 1200; 276: 0.07; 277: 1489.1566; 281: 848.88; 282: 1002.053; 283: 671.965; 284: 2705.053; 285: 776.32; 286: 77.632; 287: 6081.903; 288: 4196.288; 289: 332.9524; 290: 4529.2404; 292: 4529.2404; 293: 10611.1434; 294: 1372.5; 295: 16603.5646; 296: 17976.0646; 297: 2717.5442; 298: 177574.6; 299: 1; 300: 380944.2068; 301: 561236.351; 302: 571847.4944; 304: 131877.2483; 305: 355416.9415
|  |  | 8303-01-03 | Selective Catalytic Reduction (SCR) | SCR |  | 1: 12; 33: #N/A; 45: 8303-01-03; 46: 3; 47: Selective Catalytic Reduction (SCR); 48: SCR; 49: 4 - Custom; 50: Primary fuel Oil - Kerosene K1; 54: 25; 64: 0.09855; 65: 25; 66: 0.61347; 67: 0.61347; 68: 0.61347; 71: 3.9681; 72: 0.8661; 73: 0.8661; 74: 0.8661; 78: 0.09951; 79: 25.2378; 80: 0.22763; 81: 1.4724; 82: 0.8661; 83: 0.86607; 84: 0.8661; 86: Selective Catalytic Reduction (SCR); 88: 2730000; 89: 2550000; 90: 2550000; 91: 0; 104: 2550000; 123: 2550000; 124: 1; 125: 2550000; 137: 0; 146: 2550000; 148: 180000; 149: 2730000; 150: 2550000; 151: 2550000; 152: 1; 153: 0; 154: 0; 155: 0; 156: 0; 157: 2550000; 158: 1; 159: 0; 160: 0; 161: 0; 162: 0; 163: 0; 164: 0; 165: 2550000; 168: 0; 169: 127500; 172: 0; 173: 0; 178: 2730000; 179: 2730000; 180: 0; 181: 136500; 182: 366893; 183: 92753; 184: 3.9681; 185: 0.0031587; 192: 109200; 193: 257693; 194: 366893; 199: 109200; 200: 257693; 201: 366893; 202: 366893; 203: 0; 205: 92753; 206: 249185.1876; 207: 4; 208: 2550000; 209: 0; 210: 0; 212: 2550000; 213: 127500; 215: 0; 218: 0; 223: 2550000; 225: 180000; 226: 2730000; 227: same TCC; 228: 136500; 236: 1; 238: 109200; 239: 109200; 240: 109200; 243: 109200; 244: 0.29763; 245: 109200; 246: 0.29763; 247: 1; 248: 257692.6873; 249: 366892.6873; 250: 366893; 251: 8.5235e-07; 252: stk added + 0%; 255: 92459.9393; 256: 249184.9752; 257: 20; 258: SCR; 259: 2550000; 260: 2550000; 264: 1453000; 265: 2513690; 266: 2513690; 270: 2513690; 271: 2; 272: 20; 273: 4575; 274: 1.4724; 275: 1200; 276: 0.07; 277: 1489.1566; 281: 848.88; 282: 916.9925; 283: 614.9244; 284: 2705.053; 285: 776.32; 286: 77.632; 287: 5939.802; 288: 2098.144; 289: 188.5267; 290: 2286.6708; 292: 2286.6708; 293: 8226.4727; 294: 1372.5; 295: 16603.5646; 296: 17976.0646; 297: 1372.0024; 298: 100547.6; 299: 1; 300: 215701.039; 301: 317620.6415; 302: 325847.1142; 304: 82116.1213; 305: 221307.7771
|  |  | 8303-01-04 | HPWI with Cookie Cutter Air Deflectors | HPWI |  | 1: 13; 33: #N/A; 45: 8303-01-04; 46: 4; 47: HPWI with Cookie Cutter Air Deflectors; 48: HPWI; 49: 4 - Custom; 50: Primary fuel Oil - Kerosene K1; 54: 50; 64: 0.1971; 65: 50; 66: 1.2269; 67: 1.2269; 68: 1.2269; 71: 3.3547; 72: 0.7322; 73: 0.7322; 74: 0.7322; 78: 0.19902; 79: 50.4755; 80: 0.45526; 81: 1.2447; 82: 0.7322; 83: 0.73214; 84: 0.7322; 86: HPWI with Cookie Cutter Air Deflectors; 88: 1005000; 89: 700000; 90: 600000; 91: 0; 95: 100000; 104: 700000; 106: 125000; 107: 100000; 108: 0; 112: 25000; 121: 125000; 123: 825000; 124: 1; 125: 825000; 137: 0; 146: 825000; 148: 180000; 149: 1005000; 150: 825000; 151: 700000; 152: 0.84848; 153: 125000; 154: 0.15152; 155: 0; 156: 0; 157: 825000; 158: 1; 159: 0; 160: 0; 161: 0; 162: 0; 163: 0; 164: 0; 165: 825000; 168: 0; 169: 41250; 172: 0; 173: 0; 178: 1005000; 179: 1005000; 180: 0; 181: 50250; 182: 135065; 183: 40565; 184: 3.3547; 185: 0.0074695; 192: 40200; 193: 94865; 194: 135065; 199: 40200; 200: 94865; 201: 135065; 202: 135065; 203: 0; 205: 40565; 206: 108508.4605; 207: 4; 208: 825000; 209: 0; 210: 0; 212: 825000; 213: 41250; 215: 0; 218: 0; 223: 825000; 225: 180000; 226: 1005000; 227: same TCC; 228: 50250; 236: 1; 238: 40200; 239: 40200; 240: 40200; 243: 40200; 244: 0.29763; 245: 40200; 246: 0.29763; 247: 1; 248: 94864.8904; 249: 135064.8904; 250: 135065; 251: 8.1167e-07; 252: stk added + 0%; 255: 40261.9681; 256: 108508.3725; 257: 20; 258: Combined; 259: 825000; 260: 700000; 261: 125000; 264: N/A; 266: 1725675; 267: 125000; 270: 1850675; 271: 1; 272: 20; 273: 4575; 274: 1.2447; 278: 12479.5417; 279: 8735.6792; 280: 17.4527; 281: 388.16; 284: 290.8036; 287: 678.9636; 288: 2098.144; 289: 138.8006; 290: 2236.9446; 292: 2236.9446; 293: 2915.9082; 294: 32025; 295: 5000; 296: 37025; 297: 1342.1668; 298: 74027; 299: 1; 300: 158807.379; 301: 234176.5457; 302: 237092.4539; 304: 70675.7233; 305: 190475.2318
|  |  | 8303-01-05 | High Pressure Water Injection (HPWI) - Oil Kerosene K1 | HPWI |  | 1: 14; 33: #N/A; 45: 8303-01-05; 46: 5; 47: High Pressure Water Injection (HPWI) - Oil Kerosene K1; 48: HPWI; 49: 4 - Custom; 50: Primary fuel Oil - Kerosene K1; 51: 50 hrs/year operation; 54: 75; 64: 0.29565; 65: 75; 66: 1.8404; 67: 1.8404; 68: 1.8404; 71: 2.7412; 72: 0.5983; 73: 0.5983; 74: 0.5983; 75: CAIR OS - max within last 3 yrs; 78: 0.29853; 79: 75.7133; 80: 0.68289; 81: 1.0171; 82: 0.5983; 83: 0.59821; 84: 0.5983; 86: High Pressure Water Injection (HPWI) - Oil Kerosene K1; 88: 880000; 89: 700000; 90: 600000; 91: 0; 95: 100000; 104: 700000; 123: 700000; 124: 1; 125: 700000; 137: 0; 146: 700000; 148: 180000; 149: 880000; 150: 700000; 151: 600000; 152: 0.85714; 153: 100000; 154: 0.14286; 155: 0; 156: 0; 157: 700000; 158: 1; 159: 0; 160: 0; 161: 0; 162: 0; 163: 0; 164: 0; 165: 700000; 168: 0; 169: 35000; 172: 0; 173: 0; 178: 880000; 179: 880000; 180: 0; 181: 44000; 182: 118266; 183: 43744; 184: 2.7412; 185: 0.013711; 192: 35200; 193: 83066; 194: 118266; 199: 35200; 200: 83066; 201: 118266; 202: 118266; 203: 0; 205: 43744; 206: 116276.2263; 207: 4; 208: 700000; 209: 0; 210: 0; 212: 700000; 213: 35000; 215: 0; 218: 0; 223: 700000; 225: 180000; 226: 880000; 227: same TCC; 228: 44000; 236: 1; 238: 35200; 239: 35200; 240: 35200; 243: 35200; 244: 0.29763; 245: 35200; 246: 0.29763; 247: 1; 248: 83065.7747; 249: 118265.7747; 250: 118266; 251: 1.9054e-06; 252: stk added + 0%; 255: 43144.1435; 256: 116276.0048; 257: 20; 258: HPWI; 259: 700000; 260: 700000; 264: 997500; 265: 1725675; 266: 1725675; 270: 1725675; 271: 1; 272: 20; 273: 4575; 274: 1.0171; 278: 12479.5417; 279: 8735.6792; 280: 17.4527; 281: 388.16; 284: 290.8036; 287: 678.9636; 288: 2098.144; 289: 129.4256; 290: 2227.5696; 292: 2227.5696; 293: 2906.5332; 294: 32025; 295: 5000; 296: 37025; 297: 1336.5418; 298: 69027; 299: 1; 300: 148081.0643; 301: 218444.6061; 302: 221351.1393; 304: 80750.3723; 305: 217627.0033
|  |  | 8303-01-06 | Dual Fuel (Natural Gas with Liquid Backup) | Nat Gas |  | 1: 15; 33: #N/A; 45: 8303-01-06; 46: 6; 47: Dual Fuel (Natural Gas with Liquid Backup); 48: Nat Gas; 49: 4 - Custom; 50: Natural Gas with Oil backup; 54: 120; 64: 0.47304; 65: 120; 66: 2.9447; 67: 2.9447; 68: 2.9447; 71: 1.6369; 72: 0.35728; 73: 0.35728; 74: 0.35728; 78: 0.47765; 79: 121.1413; 80: 1.0926; 81: 0.60738; 82: 0.35728; 83: 0.35714; 84: 0.35728; 86: Dual Fuel (Natural Gas with Liquid Backup); 88: 2860000; 89: 2500000; 91: 500000; 95: 1000000; 96: 1000000; 104: 2500000; 123: 2500000; 124: 1; 125: 2500000; 137: 0; 146: 2500000; 148: 360000; 149: 2860000; 150: 2500000; 153: 1500000; 154: 0.6; 155: 1000000; 156: 0.4; 157: 2500000; 158: 1; 159: 0; 160: 0; 161: 0; 162: 0; 163: 0; 164: 0; 165: 2500000; 168: 0; 169: 125000; 172: 0; 173: 0; 178: 2860000; 179: 2860000; 180: 0; 181: 143000; 182: 384364; 183: 234808; 184: 1.6369; 185: -2.5577e-06; 192: 114400; 193: 269964; 194: 384364; 199: 114400; 200: 269964; 201: 384364; 202: 384364; 203: 0; 205: 234808; 207: 4; 208: 2500000; 209: 0; 210: 0; 212: 2500000; 213: 125000; 215: 0; 218: 0; 223: 2500000; 225: 360000; 226: 2860000; 227: same TCC; 228: 143000; 236: 1; 238: 114400; 239: 114400; 240: 114400; 243: 114400; 244: 0.29763; 245: 114400; 246: 0.29763; 247: 1; 248: 269963.7676; 249: 384363.7676; 250: 384364; 251: 6.0457e-07; 252: stk added + 0%; 255: 234808.4586; 256: 632822.6082; 257: 20; 258: Nat Gas; 259: 2500000; 260: 2500000; 264: N/A; 266: 2500000; 270: 2500000; 271: 1; 272: 20; 273: 4575; 274: 0.60738; 278: 12479.5417; 279: 8735.6792; 280: 17.4527; 281: 388.16; 284: 290.8036; 287: 678.9636; 288: 2098.144; 289: 187.5; 290: 2285.644; 292: 2285.644; 293: 2964.6076; 294: 32025; 295: 5000; 296: 37025; 297: 1371.3864; 298: 100000; 299: 1; 300: 214526.2931; 301: 315897.6795; 302: 318862.287; 304: 194793.4963; 305: 524979.9309
|  |  | 8303-01-07 | LM2500 DLE - new gas fired GE turbine | New Eqp |  | 1: 16; 33: #N/A; 45: 8303-01-07; 46: 7; 47: LM2500 DLE - new gas fired GE turbine; 48: New Eqp; 49: 4 - Custom; 50: Natural Gas with Oil backup; 54: 25; 64: 0.09855; 65: 25; 66: 0.61347; 67: 0.61347; 68: 0.61347; 71: 3.9681; 72: 0.8661; 73: 0.8661; 74: 0.8661; 78: 0.09951; 79: 25.2378; 80: 0.22763; 81: 1.4724; 82: 0.8661; 83: 0.86607; 84: 0.8661; 86: LM2500 DLE - new gas fired GE turbine; 88: 12360000; 89: 12000000; 90: 12000000; 91: 0; 104: 12000000; 106: 1500000; 107: 1000000; 108: 500000; 121: 1500000; 123: 13500000; 124: 1; 125: 13500000; 137: 0; 146: 13500000; 147: 1500000; 148: 360000; 149: 12360000; 150: 13500000; 151: 13000000; 152: 0.96296; 153: 500000; 154: 0.037037; 155: 0; 156: 0; 157: 13500000; 158: 1; 159: 0; 160: 0; 161: 0; 162: 0; 163: 0; 164: 0; 165: 13500000; 168: 0; 169: 675000; 172: 0; 173: 0; 178: 12360000; 179: 12360000; 180: 0; 181: 618000; 182: 1661097; 183: 418610; 184: 3.9681; 185: 1.3055e-07; 192: 494400; 193: 1166697; 194: 1661097; 199: 494400; 200: 1166697; 201: 1661097; 202: 1661097; 203: 0; 205: 418610; 206: 1128178.4268; 207: 4; 208: 13500000; 209: 0; 210: 0; 212: 13500000; 213: 675000; 215: 0; 218: 0; 223: 13500000; 224: 1500000; 225: 360000; 226: 12360000; 227: same TCC; 228: 618000; 236: 1; 238: 494400; 239: 494400; 240: 494400; 243: 494400; 244: 0.29763; 245: 494400; 246: 0.29763; 247: 1; 248: 1166696.5622; 249: 1661096.5622; 250: 1661097; 251: 2.6357e-07; 252: stk added + 0%; 255: 418609.835; 256: 1128178.1295; 257: 20; 258: New Eqp; 259: 13500000; 260: 13500000; 264: N/A; 266: 13500000; 270: 13500000; 271: 2; 272: 20; 273: 4575; 274: 1.4724; 275: 1200; 276: 0.07; 277: 1489.1566; 281: 848.88; 282: 916.9925; 283: 614.9244; 284: 2705.053; 285: 776.32; 286: 77.632; 287: 5939.802; 288: 2098.144; 289: 1012.5; 290: 3110.644; 292: 3110.644; 293: 9050.446; 294: 1372.5; 295: 16603.5646; 296: 17976.0646; 297: 1866.3864; 298: 540000; 299: 1; 300: 1158441.9825; 301: 1700308.3689; 302: 1709358.8149; 304: 430772.315; 305: 1160956.7284
|  |  | 8303-01-08 | LM2500 - new oil fired GE turbine | New Eqp |  | 1: 17; 33: #N/A; 45: 8303-01-08; 46: 8; 47: LM2500 - new oil fired GE turbine; 48: New Eqp; 49: 4 - Custom; 50: Primary fuel Oil - Kerosene K1; 54: 42; 64: 0.16556; 65: 42; 66: 1.0306; 67: 1.0306; 68: 1.0306; 71: 3.551; 72: 0.77505; 73: 0.77505; 74: 0.77505; 78: 0.16718; 79: 42.3995; 80: 0.38242; 81: 1.3176; 82: 0.77505; 83: 0.775; 84: 0.77505; 86: LM2500 - new oil fired GE turbine; 88: 10860000; 89: 12000000; 90: 12000000; 91: 0; 104: 12000000; 123: 12000000; 124: 1; 125: 12000000; 137: 0; 146: 12000000; 147: 1500000; 148: 360000; 149: 10860000; 150: 12000000; 151: 12000000; 152: 1; 153: 0; 154: 0; 155: 0; 156: 0; 157: 12000000; 158: 1; 159: 0; 160: 0; 161: 0; 162: 0; 163: 0; 164: 0; 165: 12000000; 168: 0; 169: 600000; 172: 0; 173: 0; 178: 10860000; 179: 10860000; 180: 0; 181: 543000; 182: 1459507; 183: 411017; 184: 3.551; 185: -3.9351e-07; 192: 434400; 193: 1025107; 194: 1459507; 199: 434400; 200: 1025107; 201: 1459507; 202: 1459507; 203: 0; 205: 411017; 206: 1107715.4284; 207: 4; 208: 12000000; 209: 0; 210: 0; 212: 12000000; 213: 600000; 215: 0; 218: 0; 223: 12000000; 224: 1500000; 225: 360000; 226: 10860000; 227: same TCC; 228: 543000; 236: 1; 238: 434400; 239: 434400; 240: 434400; 243: 434400; 244: 0.29763; 245: 434400; 246: 0.29763; 247: 1; 248: 1025107.1736; 249: 1459507.1736; 250: 1459507; 251: -1.1892e-07; 252: -1.1892e-07; 255: 411017.2106; 256: 1107715.5601; 257: 20; 258: New Eqp; 259: 12000000; 260: 12000000; 264: N/A; 266: 12000000; 270: 12000000; 271: 2; 272: 20; 273: 4575; 274: 1.3176; 275: 1200; 276: 0.07; 277: 1489.1566; 281: 848.88; 282: 820.5907; 283: 550.2785; 284: 2705.053; 285: 776.32; 286: 77.632; 287: 5778.7542; 288: 2098.144; 289: 900; 290: 2998.144; 292: 2998.144; 293: 8776.8982; 294: 1372.5; 295: 16603.5646; 296: 17976.0646; 297: 1798.8864; 298: 480000; 299: 1; 300: 1029726.2066; 301: 1511525.093; 302: 1520301.9912; 304: 428137.864; 305: 1153856.7279
18
8304-01 | NPU | TRBINE | 8304-01-01 | SCR + HPWI + Dual Fuel (Nat Gas - oil backup) | SCR |  | 19 | 11 | 4 | Norwich Public Utilities | 8304 | 8304-01 | Norwich | TRBINE | 1 |  | 18.8 | 18.8 | Combustion Turbine | Rolls Royce | Olympus B |  | 1972 | 55 yrs | No. 2 oil |  | 0.553 | 141.31 | 0.62 |  | 50 hrs/yr operation | 50 | [5 empty] | 50 | 9900 | 9900 | 0.553 | 141.31 | 2.7374 | CAIR-OS (max last 3 yrs) | 19 | 4811 | 0.62 | 158.4307 | 1.5 |  | 8304-01-01 | 1 | SCR + HPWI + Dual Fuel (Nat Gas - oil backup) | SCR | 3- Alternate | Natural Gas with Oil backup | [13 empty] | 0.02348 | 6 | 0.11623 | 0.11623 | 0.11623 |  |  | 2.6211 | 0.95754 | 0.95754 | 0.95754 | CAIR OS - max within last 3 yrs |  |  | 0.026477 | 6.7269 | 0.06369 | 1.4363 | 0.95754 | 0.9573 | 0.95754 |  | SCR + HPWI + Dual Fuel (Nat Gas - oil backup) |  | 7319263 | 1801351 | 1801351 | 0 | [12 empty] | 1801351 |  | 1782826 | 1782826 | 0 | [12 empty] | 1782826 |  | 3584177 | 1 | 3584177 |  | 1396073 |  | 1396073 | [5 empty] | 384621 | 545647 | 930268 | 472841.44 | 139607.3 |  | 612448.74 |  |  | 326148.337 | 326148.337 | 7175263.414 |  | 144000 | 7319263.414 | 3584177 | 3584177 | 1 | 0 | 0 | 0 | 0 | 3584177 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3584177 |  |  | 0 | 190647.7128 | 1396073 | 0.38951 | 930268 | 0.25955 |  | 612448.74 | 0.17088 |  | 7319263.414 | 7319263.414 | 5.6563e-08 | 389322.522 | 910464.9024 | 347672 | 2.6211 | 0.00090643 | [6 empty] | 219577.9024 | 690887 | 910464.9024 |  |  |  |  | 219577.9024 | 690887 | 910464.9024 | 910464.9024 | 0 |  | 347672 | 633891.5348 | 3 | 3584177 | 0 | 0 |  | 3584177 | 190647.7128 | 1396073 | 930268 | 472841.44 | 139607.3 | 612448.74 |  |  | 326148.337 | 326148.337 | 7175263.414 |  | 144000 | 7319263.414 | same TCC | 389322.522 | [7 empty] | 1 |  | 292770.5366 | 292770.5366 | 292770.5366 |  |  | 292770.5366 | 0.29763 | 292770.5366 | 0.29763 | 1 | 690886.6879 | 983657.2245 | 910464.9024 | -0.08039 | -0.08039 |  |  | 375280.8971 | 684850.1091 | 18.8 | Combined | 7175263.414 | 3362772.996 | 1047551.582 | 2764938.836 |  | N/A |  | 2410512.8 | 1652392.2 | 2764938.836 |  | 6827843.836 | 2 | 19 | 4811 | 1.4363 | 1263.1579 | 0.07 | 1399.8072 |  |  |  | 806.436 | 894.534 | 599.864 | 2542.7498 | 693.2538 | 69.3254 | 5606.163 | 3986.4736 | 486.4839 | 4472.9575 |  | 4472.9575 | 10079.1204 | 1443.3 | 16544.9046 | 17988.2046 | 2683.7745 | 273113.7534 | 1 | 585900.8111 | 861698.339 | 871777.4594 |  | 332596.9849 | 606956.2377
|  |  | 8304-01-02 | SCR + Water Injection (HPWI) - oil # 2 | SCR |  | 1: 20; 33: #N/A; 45: 8304-01-02; 46: 2; 47: SCR + Water Injection (HPWI) - oil # 2; 48: SCR; 49: 3- Alternate; 50: Primary fuel No. 2 oil; 64: 0.03522; 65: 9; 66: 0.17434; 67: 0.17434; 68: 0.17434; 71: 2.563; 72: 0.93631; 73: 0.93631; 74: 0.93631; 78: 0.039715; 79: 10.0904; 80: 0.095535; 81: 1.4045; 82: 0.93631; 83: 0.93594; 84: 0.93631; 86: SCR + Water Injection (HPWI) - oil # 2; 88: 4554325; 89: 1801351; 90: 1801351; 91: 0; 104: 1801351; 106: 303165; 107: 303165; 108: 0; 121: 303165; 123: 2104516; 124: 1; 125: 2104516; 127: 948871; 129: 948871; 135: 230472; 136: 340677; 137: 571149; 138: 289962.88; 139: 94887.1; 141: 384849.98; 144: 200469.299; 145: 200469.299; 146: 4410324.578; 148: 144000; 149: 4554324.578; 150: 2104516; 151: 2104516; 152: 1; 153: 0; 154: 0; 155: 0; 156: 0; 157: 2104516; 158: 1; 159: 0; 160: 0; 161: 0; 162: 0; 163: 0; 164: 0; 165: 2104516; 168: 0; 169: 111942.3404; 170: 948871; 171: 0.45087; 172: 571149; 173: 0.27139; 175: 384849.98; 176: 0.18287; 178: 4554324.578; 179: 4554324.578; 180: -9.2659e-08; 181: 242251.3073; 182: 566525.7373; 183: 221348; 184: 2.563; 185: 0.0013945; 192: 136629.7373; 193: 429896; 194: 566525.7373; 199: 136629.7373; 200: 429896; 201: 566525.7373; 202: 566525.7373; 203: 0; 205: 221348; 206: 403374.6602; 207: 3; 208: 2104516; 209: 0; 210: 0; 212: 2104516; 213: 111942.3404; 214: 948871; 215: 571149; 216: 289962.88; 217: 94887.1; 218: 384849.98; 221: 200469.299; 222: 200469.299; 223: 4410324.578; 225: 144000; 226: 4554324.578; 227: same TCC; 228: 242251.3073; 236: 1; 238: 182172.9831; 239: 182172.9831; 240: 182172.9831; 243: 182172.9831; 244: 0.29763; 245: 182172.9831; 246: 0.29763; 247: 1; 248: 429896.0217; 249: 612069.0048; 250: 566525.7373; 251: -0.08039; 252: -0.08039; 255: 238808.7768; 256: 435802.1368; 257: 18.8; 258: Combined; 259: 4410324.578; 260: 3362772.996; 261: 1047551.582; 264: N/A; 266: 2410512.8; 267: 1652392.2; 270: 4062905; 271: 2; 272: 19; 273: 4811; 274: 1.4045; 275: 1263.1579; 276: 0.07; 277: 1399.8072; 281: 806.436; 282: 874.701; 283: 586.5642; 284: 2542.7498; 285: 693.2538; 286: 69.3254; 287: 5573.0302; 288: 3986.4736; 289: 289.482; 290: 4275.9556; 292: 4275.9556; 293: 9848.9858; 294: 1443.3; 295: 16544.9046; 296: 17988.2046; 297: 2565.5733; 298: 162516.2; 299: 1; 300: 348639.9795; 301: 513721.7528; 302: 523570.7386; 304: 204279.7244; 305: 372790.0691
|  |  | 8304-01-03 | Selective Catalytic Reduction (SCR) | SCR |  | 1: 21; 33: #N/A; 45: 8304-01-03; 46: 3; 47: Selective Catalytic Reduction (SCR); 48: SCR; 49: 3- Alternate; 50: Primary fuel No. 2 oil; 64: 0.097835; 65: 25; 66: 0.48428; 67: 0.48428; 68: 0.48428; 71: 2.2531; 72: 0.82308; 73: 0.82308; 74: 0.9; 78: 0.062357; 79: 15.8431; 80: 0.15; 81: 1.35; 82: 0.9; 83: 0.89942; 84: 0.9; 85: 0.9; 86: Selective Catalytic Reduction (SCR); 88: 3386773; 89: 1801351; 90: 1801351; 91: 0; 104: 1801351; 123: 1801351; 124: 1; 125: 1801351; 127: 562086; 129: 562086; 135: 189075; 136: 226060; 137: 415135; 138: 222285.76; 139: 56208.6; 141: 278494.36; 144: 152853.318; 145: 152853.318; 146: 3362772.996; 148: 24000; 149: 3386772.996; 150: 1801351; 151: 1801351; 152: 1; 153: 0; 154: 0; 155: 0; 156: 0; 157: 1801351; 158: 1; 159: 0; 160: 0; 161: 0; 162: 0; 163: 0; 164: 0; 165: 1801351; 168: 0; 169: 95816.5426; 170: 562086; 171: 0.31204; 172: 415135; 173: 0.23046; 175: 278494.36; 176: 0.1546; 178: 3386772.996; 179: 3386772.996; 180: -1.1811e-09; 181: 180147.4998; 182: 421290.1899; 183: 187812; 184: 2.2531; 185: 0.0044031; 192: 101603.1899; 193: 319687; 194: 421290.1899; 199: 101603.1899; 200: 319687; 201: 421290.1899; 202: 421290.1899; 203: 0; 205: 187812; 206: 312066.8073; 207: 3; 208: 1801351; 209: 0; 210: 0; 212: 1801351; 213: 95816.5426; 214: 562086; 215: 415135; 216: 222285.76; 217: 56208.6; 218: 278494.36; 221: 152853.318; 222: 152853.318; 223: 3362772.996; 225: 24000; 226: 3386772.996; 227: same TCC; 228: 180147.4998; 236: 1; 238: 135470.9198; 239: 135470.9198; 240: 135470.9198; 243: 135470.9198; 244: 0.29763; 245: 135470.9198; 246: 0.29763; 247: 1; 248: 319687.4119; 249: 455158.3318; 250: 421290.1899; 251: -0.080391; 252: -0.080391; 255: 202017.0418; 256: 337154.3198; 257: 18.8; 258: SCR; 259: 3362772.996; 260: 3362772.996; 264: 1393360; 265: 2410512.8; 266: 2410512.8; 270: 2410512.8; 271: 2; 272: 19; 273: 4811; 274: 1.35; 275: 1263.1579; 276: 0.07; 277: 1399.8072; 281: 806.436; 282: 840.78; 283: 563.8172; 284: 2542.7498; 285: 693.2538; 286: 69.3254; 287: 5516.3621; 288: 1993.2368; 289: 171.749; 290: 2164.9858; 292: 2164.9858; 293: 7681.348; 294: 1443.3; 295: 16544.9046; 296: 17988.2046; 297: 1298.9915; 298: 96420.512; 299: 1; 300: 206847.3501; 301: 304566.8536; 302: 312248.2016; 304: 138587.9454; 305: 231294.9642
|  |  | 8304-01-04 | High Pressure Water Injection (HPWI) | HPWI |  | 1: 22; 33: #N/A; 45: 8304-01-04; 46: 4; 47: High Pressure Water Injection (HPWI); 48: HPWI; 49: 3- Alternate; 50: Natural Gas with Oil backup; 64: 0.18393; 65: 47; 66: 0.91045; 67: 0.91045; 68: 0.91045; 71: 1.8269; 72: 0.6674; 73: 0.6674; 74: 0.6674; 75: CAIR OS - max within last 3 yrs; 78: 0.2074; 79: 52.6944; 80: 0.4989; 81: 1.0011; 82: 0.6674; 83: 0.66548; 84: 0.6674; 86: High Pressure Water Injection (HPWI); 88: 1191552; 89: 303165; 90: 303165; 91: 0; 104: 303165; 123: 303165; 124: 1; 125: 303165; 127: 386785; 129: 386785; 135: 41397; 136: 114617; 137: 156014; 138: 67677.12; 139: 38678.5; 141: 106355.62; 144: 47615.981; 145: 47615.981; 146: 1047551.582; 148: 144000; 149: 1191551.582; 150: 303165; 151: 303165; 152: 1; 153: 0; 154: 0; 155: 0; 156: 0; 157: 303165; 158: 1; 159: 0; 160: 0; 161: 0; 162: 0; 163: 0; 164: 0; 165: 303165; 168: 0; 169: 16125.7979; 170: 386785; 171: 1.2758; 172: 156014; 173: 0.51462; 175: 106355.62; 176: 0.35082; 178: 1191551.582; 179: 1191551.582; 180: -3.508e-07; 181: 63380.4033; 182: 148220.5475; 183: 81969; 184: 1.8269; 185: 0.010209; 192: 35746.5475; 193: 112474; 194: 148220.5475; 199: 35746.5475; 200: 112474; 201: 148220.5475; 202: 148220.5475; 203: 0; 205: 81969; 206: 148058.1456; 207: 3; 208: 303165; 209: 0; 210: 0; 212: 303165; 213: 16125.7979; 214: 386785; 215: 156014; 216: 67677.12; 217: 38678.5; 218: 106355.62; 221: 47615.981; 222: 47615.981; 223: 1047551.582; 225: 144000; 226: 1191551.582; 227: same TCC; 228: 63380.4033; 236: 1; 238: 47662.0633; 239: 47662.0633; 240: 47662.0633; 243: 47662.0633; 244: 0.29763; 245: 47662.0633; 246: 0.29763; 247: 1; 248: 112474.04; 249: 160136.1033; 250: 148220.5475; 251: -0.080391; 252: -0.080391; 255: 87654.4719; 256: 159960.6458; 257: 18.8; 258: HPWI; 259: 1047551.582; 260: 1047551.582; 264: 955140; 265: 1652392.2; 266: 1652392.2; 270: 1652392.2; 271: 1; 272: 19; 273: 4811; 274: 1.0011; 278: 13813.9949; 279: 9669.7964; 280: 19.3189; 281: 368.752; 284: 305.8046; 287: 674.5566; 288: 1993.2368; 289: 117.7329; 290: 2110.9697; 292: 2110.9697; 293: 2785.5263; 294: 33677; 295: 4750; 296: 38427; 297: 1266.5818; 298: 66095.688; 299: 1; 300: 141792.6293; 301: 209154.8992; 302: 211940.4255; 304: 116010.8539; 305: 211708.2072
|  |  | 8304-01-05 | Dual Fuel (Natural Gas with Liquid Backup) | Nat Gas |  | 1: 23; 33: #N/A; 45: 8304-01-05; 46: 5; 47: Dual Fuel (Natural Gas with Liquid Backup); 48: Nat Gas; 49: 3- Alternate; 50: Natural Gas with Oil backup; 64: 0.3522; 65: 90; 66: 1.7434; 67: 1.7434; 68: 1.7434; 71: 0.99394; 72: 0.3631; 73: 0.3631; 74: 0.3631; 78: 0.39715; 79: 100.9042; 80: 0.95535; 81: 0.54465; 82: 0.3631; 83: 0.35943; 84: 0.3631; 86: Dual Fuel (Natural Gas with Liquid Backup); 88: 2908939; 89: 1479661; 90: 1479661; 91: 0; 104: 1479661; 123: 1479661; 124: 1; 125: 1479661; 127: 447202; 129: 447202; 135: 154149; 136: 204970; 137: 359119; 138: 182878.56; 139: 44720.2; 141: 227598.76; 144: 125679.038; 145: 125679.038; 146: 2764938.836; 148: 144000; 149: 2908938.836; 150: 1479661; 151: 1479661; 152: 1; 153: 0; 154: 0; 155: 0; 156: 0; 157: 1479661; 158: 1; 159: 0; 160: 0; 161: 0; 162: 0; 163: 0; 164: 0; 165: 1479661; 168: 0; 169: 78705.3723; 170: 447202; 171: 0.30223; 172: 359119; 173: 0.2427; 175: 227598.76; 176: 0.15382; 178: 2908938.836; 179: 2908938.836; 180: -5.6378e-08; 181: 154730.7891; 182: 361851.1651; 183: 364103; 184: 0.99394; 185: 0.00012371; 192: 87268.1651; 193: 274583; 194: 361851.1651; 199: 87268.1651; 200: 274583; 201: 361851.1651; 202: 361851.1651; 203: 0; 205: 364103; 207: 3; 208: 1479661; 209: 0; 210: 0; 212: 1479661; 213: 78705.3723; 214: 447202; 215: 359119; 216: 182878.56; 217: 44720.2; 218: 227598.76; 221: 125679.038; 222: 125679.038; 223: 2764938.836; 225: 144000; 226: 2908938.836; 227: same TCC; 228: 154730.7891; 236: 1; 238: 116357.5534; 239: 116357.5534; 240: 116357.5534; 243: 116357.5534; 244: 0.29763; 245: 116357.5534; 246: 0.29763; 247: 1; 248: 274583.2475; 249: 390940.801; 250: 361851.1651; 251: -0.080391; 252: -0.080391; 255: 393324.9987; 256: 717778.7902; 257: 18.8; 258: Nat Gas; 259: 2764938.836; 260: 2764938.836; 264: N/A; 266: 2764938.836; 270: 2764938.836; 271: 1; 272: 19; 273: 4811; 274: 0.54465; 278: 13813.9949; 279: 9669.7964; 280: 19.3189; 281: 368.752; 284: 305.8046; 287: 674.5566; 288: 1993.2368; 289: 197.0019; 290: 2190.2387; 292: 2190.2387; 293: 2864.7953; 294: 33677; 295: 4750; 296: 38427; 297: 1314.1432; 298: 110597.5534; 299: 1; 300: 237260.8316; 301: 349172.5283; 302: 352037.3236; 304: 354184.2639; 305: 646350.8633
|  |  | 8304-01-06 | Solar Titan 130 - new dual fuel w/ SoLoNOx | New Eqp |  | 1: 24; 33: #N/A; 45: 8304-01-06; 46: 6; 47: Solar Titan 130 - new dual fuel w/ SoLoNOx; 48: New Eqp; 49: 3- Alternate; 50: Natural Gas with Oil backup; 64: 0.058701; 65: 15; 66: 0.29057; 67: 0.29057; 68: 0.29057; 71: 2.4468; 72: 0.89385; 73: 0.89385; 74: 0.89385; 78: 0.066192; 79: 16.8174; 80: 0.15922; 81: 1.3408; 82: 0.89385; 83: 0.89324; 84: 0.89385; 86: Solar Titan 130 - new dual fuel w/ SoLoNOx; 88: 13622600; 89: 9750000; 90: 9750000; 91: 0; 104: 9750000; 123: 9750000; 124: 1; 125: 9750000; 127: 940000; 129: 940000; 135: 750000; 136: 960000; 137: 1710000; 138: 992000; 139: 94000; 141: 1086000; 144: 674300; 145: 674300; 146: 14834600; 147: 1500000; 148: 288000; 149: 13622600; 150: 9750000; 151: 9750000; 152: 1; 153: 0; 154: 0; 155: 0; 156: 0; 157: 9750000; 158: 1; 159: 0; 160: 0; 161: 0; 162: 0; 163: 0; 164: 0; 165: 9750000; 168: 0; 169: 518617.0213; 170: 940000; 171: 0.09641; 172: 1710000; 173: 0.17538; 175: 1086000; 176: 0.11138; 178: 13622600; 179: 13622600; 180: 0; 181: 724606.383; 182: 1694555; 183: 692571; 184: 2.4468; 185: 8.7547e-06; 192: 408678; 193: 1285877; 194: 1694555; 199: 408678; 200: 1285877; 201: 1694555; 202: 1694555; 203: 0; 205: 692571; 206: 1263861.7531; 207: 3; 208: 9750000; 209: 0; 210: 0; 212: 9750000; 213: 518617.0213; 214: 940000; 215: 1710000; 216: 992000; 217: 94000; 218: 1086000; 221: 674300; 222: 674300; 223: 14834600; 224: 1500000; 225: 288000; 226: 13622600; 227: same TCC; 228: 724606.383; 236: 1; 238: 544904; 239: 544904; 240: 544904; 243: 544904; 244: 0.29763; 245: 544904; 246: 0.29763; 247: 1; 248: 1285877.0702; 249: 1830781.0702; 250: 1694555; 251: -0.08039; 252: -0.08039; 255: 748240.5564; 256: 1365464.1915; 257: 18.8; 258: Combined; 259: 14834600; 260: 14834600; 264: N/A; 266: 14834600; 270: 14834600; 271: 2; 272: 19; 273: 4811; 274: 1.3408; 275: 1263.1579; 276: 0.07; 277: 1399.8072; 281: 806.436; 282: 835.035; 283: 559.9647; 284: 2542.7498; 285: 693.2538; 286: 69.3254; 287: 5506.7647; 288: 1993.2368; 289: 1056.9652; 290: 3050.202; 292: 3050.202; 293: 8556.9667; 294: 1443.3; 295: 16544.9046; 296: 17988.2046; 297: 1830.1212; 298: 593384; 299: 1; 300: 1272964.6988; 301: 1868178.82; 302: 1876735.7867; 304: 767022.2574; 305: 1399738.9176
|  |  | 8304-01-07 | Solar Titan 130 - new oil fired turbine | New Eqp |  | 1: 25; 33: #N/A; 45: 8304-01-07; 46: 7; 47: Solar Titan 130 - new oil fired turbine; 48: New Eqp; 49: 3- Alternate; 50: Primary fuel No. 2 oil; 64: 0.25437; 65: 65; 66: 1.2591; 67: 1.2591; 68: 1.2591; 71: 1.4782; 72: 0.54002; 73: 0.54002; 74: 0.54002; 78: 0.28683; 79: 72.8752; 80: 0.68997; 81: 0.81003; 82: 0.54002; 83: 0.53737; 84: 0.54002; 86: Solar Titan 130 - new oil fired turbine; 88: 9997875; 89: 7263410; 90: 7263410; 91: 0; 104: 7263410; 123: 7263410; 124: 1; 125: 7263410; 127: 714287; 129: 714287; 135: 652501; 136: 739586; 137: 1392087; 138: 749582.72; 139: 71428.7; 141: 821011.42; 144: 509539.771; 145: 509539.771; 146: 11209874.962; 147: 1500000; 148: 288000; 149: 9997874.962; 150: 7263410; 151: 7263410; 152: 1; 153: 0; 154: 0; 155: 0; 156: 0; 157: 7263410; 158: 1; 159: 0; 160: 0; 161: 0; 162: 0; 163: 0; 164: 0; 165: 7263410; 168: 0; 169: 386351.5957; 170: 714287; 171: 0.09834; 172: 1392087; 173: 0.19166; 175: 821011.42; 176: 0.11303; 178: 9997874.962; 179: 9997874.962; 180: -3.8008e-09; 181: 531801.8597; 182: 1243665.2489; 183: 841377; 184: 1.4782; 185: 5.9921e-05; 192: 299936.2489; 193: 943729; 194: 1243665.2489; 199: 299936.2489; 200: 943729; 201: 1243665.2489; 202: 1243665.2489; 203: 0; 205: 841377; 207: 3; 208: 7263410; 209: 0; 210: 0; 212: 7263410; 213: 386351.5957; 214: 714287; 215: 1392087; 216: 749582.72; 217: 71428.7; 218: 821011.42; 221: 509539.771; 222: 509539.771; 223: 11209874.962; 224: 1500000; 225: 288000; 226: 9997874.962; 227: same TCC; 228: 531801.8597; 236: 1; 238: 399914.9985; 239: 399914.9985; 240: 399914.9985; 243: 399914.9985; 244: 0.29763; 245: 399914.9985; 246: 0.29763; 247: 1; 248: 943728.6689; 249: 1343643.6674; 250: 1243665.2489; 251: -0.08039; 252: -0.08039; 255: 908960.9424; 256: 1658762.8239; 257: 18.8; 258: Combined; 259: 11209874.962; 260: 11209874.962; 264: N/A; 266: 11209874.962; 270: 11209874.962; 271: 2; 272: 19; 273: 4811; 274: 0.81003; 275: 1263.1579; 276: 0.07; 277: 1399.8072; 281: 806.436; 282: 504.4852; 283: 338.3018; 284: 2542.7498; 285: 693.2538; 286: 69.3254; 287: 4954.552; 288: 1993.2368; 289: 798.7036; 290: 2791.9404; 292: 2791.9404; 293: 7746.4924; 294: 1443.3; 295: 16544.9046; 296: 17988.2046; 297: 1675.1642; 298: 448394.9985; 299: 1; 300: 961925.1685; 301: 1411995.3312; 302: 1419741.8236; 304: 960440.5523; 305: 1752707.9639
26
8301-01 | PSEG | BHB4 | 8301-01-01 | Selective Catalytic Reduction (SCR) | SCR |  | 1: 27; 2: 12; 3: 5; 4: PSEG Power LLC, PSEG Fossil LLC, PSEG Power Connecticut; 5: 8301; 6: 8301-01; 7: Bridgeport Harbor Station; 8: BHB4; 9: 1; 11: 22; 12: 602; 13: Combustion Turbine; 14: Pratt & Whitney; 15: FT-4A-8LI; 16: FT; 17: Jan 1967; 18: 60 yrs; 19: Jet Fuel A (Kerosene K1); 21: 0.709; 22: 186.17; 23: 0.73; 35: 0.73; 36: 186.17; 38: CAIR-OS (max last 3 yrs); 39: 24; 40: 2366; 41: 0.68; 42: 173.4186; 43: 0.8; 45: 8301-01-01; 46: 1; 47: Selective Catalytic Reduction (SCR); 48: SCR; 49: 4 - Custom; 72: 0.9; 74: 0.9; 75: CAIR OS - max within last 3 yrs; 78: 0.067625; 79: 17.3419; 80: 0.08; 81: 0.72; 82: 0.9; 83: 0.90055; 84: 0.9; 85: 0.9; 86: Selective Catalytic Reduction (SCR); 88: 8895118; 89: 8895118; 90: 8895118; 91: 0; 104: 8895118; 123: 8895118; 124: 1; 125: 8895118; 129: 0; 137: 0; 141: 0; 146: 8895118; 149: 8895118; 150: 8895118; 151: 8895118; 152: 1; 153: 0; 154: 0; 155: 0; 156: 0; 157: 8895118; 158: 1; 159: 0; 160: 0; 161: 0; 162: 0; 163: 0; 164: 0; 165: 8895118; 168: 0; 169: 404323.5455; 170: 0; 171: 0; 172: 0; 173: 0; 175: 0; 176: 0; 178: 8895118; 179: 8895118; 180: 0; 181: 404323.5455; 183: 118997; 184: 1; 192: 355804.72; 194: 118997; 199: 355804.72; 202: 118997; 205: 118997; 206: 165273.6111; 208: 8895118; 209: 0; 210: 0; 212: 8895118; 213: 404323.5455; 218: 0; 223: 8895118; 226: 8895118; 227: same TCC; 228: 404323.5455; 236: 0; 238: 0; 247: 1; 248: 839636.2129; 249: 839636.2129; 250: 118997; 251: -6.0559; 252: -6.0559; 256: 1166161.4067; 257: 22; 258: SCR; 259: 8895118; 260: 8895118; 264: 1552400; 265: 2685652; 266: 2685652; 270: 2685652; 271: 2; 272: 24; 273: 2366; 274: 0.72; 275: 1000; 276: 0.07; 277: 1638.0723; 281: 1018.656; 282: 448.416; 283: 300.7025; 284: 2975.5583; 285: 1024.7424; 286: 102.4742; 287: 5870.5494; 288: 2517.7728; 289: 241.7087; 290: 2759.4815; 292: 2759.4815; 293: 8630.0309; 294: 709.8; 295: 16813.76; 296: 17523.56; 297: 1655.6889; 298: 107426.08; 299: 1; 300: 230457.1872; 301: 339538.9561; 302: 348168.987; 305: 483568.0375
|  |  | 8301-01-02 | High Pressure Water Injection (HPWI) | HPWI |  | 1: 28; 33: #N/A; 45: 8301-01-02; 46: 2; 47: High Pressure Water Injection (HPWI); 48: HPWI; 49: 4 - Custom; 72: 0.6; 74: 0.6; 75: CAIR OS - max within last 3 yrs; 78: 0.2705; 79: 69.3675; 80: 0.32; 81: 0.48; 82: 0.6; 83: 0.60221; 84: 0.6; 85: 0.6; 86: High Pressure Water Injection (HPWI); 88: 843728; 89: 843728; 90: 843728; 91: 0; 104: 843728; 123: 843728; 124: 1; 125: 843728; 129: 0; 137: 0; 141: 0; 146: 843728; 149: 843728; 150: 843728; 151: 843728; 152: 1; 153: 0; 154: 0; 155: 0; 156: 0; 157: 843728; 158: 1; 159: 0; 160: 0; 161: 0; 162: 0; 163: 0; 164: 0; 165: 843728; 168: 0; 169: 38351.2727; 170: 0; 171: 0; 172: 0; 173: 0; 175: 0; 176: 0; 178: 843728; 179: 843728; 180: 0; 181: 38351.2727; 183: 839358; 184: 1; 192: 33749.12; 194: 839358; 199: 33749.12; 202: 839358; 205: 839358; 206: 1748662.5; 208: 843728; 209: 0; 210: 0; 212: 843728; 213: 38351.2727; 218: 0; 223: 843728; 226: 843728; 227: same TCC; 228: 38351.2727; 236: 0; 238: 0; 247: 1; 248: 79641.9545; 249: 79641.9545; 250: 839358; 251: 0.90512; 252: stk added + 91%; 256: 165920.7384; 257: 22; 258: HPWI; 259: 843728; 260: 843728; 264: 1068100; 265: 1847813; 266: 1847813; 270: 1847813; 271: 1; 272: 24; 273: 2366; 274: 0.48; 278: 5378.2506; 279: 3764.7754; 280: 7.5215; 281: 465.792; 284: 150.3915; 287: 616.1835; 288: 2517.7728; 289: 166.3032; 290: 2684.076; 292: 2684.076; 293: 3300.2595; 294: 16562; 295: 6000; 296: 22562; 297: 1610.4456; 298: 73912.52; 299: 1; 300: 158561.7893; 301: 234084.7548; 302: 237385.0143; 305: 494552.1132
29
8300-01 | NRG | BR10 | 8300-01-01 | High Pressure Water Injection (HPWI) | HPWI |  | 30 | 13 | 6 | NRG Energy, Inc | 8300 | 8300-01 | Branford | BR10 | 1 |  | 20 | 20 | Combustion Turbine | Pratt & Whitney | FT4-A8 | FT | Jul 1969 | 57 yrs | Ultra low sulfur kerosene oil (ULSD) |  | 0.726 |  | 0.8 |  | 48 hrs/year operation | 48 |  |  |  |  | 2010-2009 average | 29 | 7735 | 7735 | 0.8 |  | 3.4 | CAIR-OS (max last 3 yrs) | 39 | 9750 | 0.73 |  | 3.5393 |  | 8300-01-01 | 1 | High Pressure Water Injection (HPWI) | HPWI | 1 - Std |  | 48 hrs/year operation | Cost Analysis not provided | [9 empty] | 2010-2009 average | Controlled NOx stk's rate is COS-COB units FLER | 0.22 |  | 0.9 | 0.9 | 0.85085 |  |  | 2.5 | 0.73529 | 0.725 | 0.725 | CAIR OS - max within last 3 yrs | Controlled NOx selected rate is COS-COB units max. last 3-yr stack rate | 103 | 0.19965 |  | 0.97329 | 2.566 | 0.725 | 0.72651 | 0.725 |  | High Pressure Water Injection (HPWI) |  | 2409779 | 1140994 | 360000 | 159400 | 40000 | 250000 |  | 109500 |  | 16000 |  | 50000 |  |  | 100000 |  | 934900 | 56094 | [17 empty] | 1140994 | 1 | 1140994 |  |  | 513447 | 513447 |  |  |  | 376528 |  |  |  | 376528 |  |  |  | 378810 |  |  |  |  | 2409779 |  |  | 2409779 | 1140994 | 360000 | 0.31551 | 558900 | 0.48984 | 0 | 0 | 918900 | 0.80535 | 16000 | 0.014023 | 50000 | 0.043821 | 100000 | 0.087643 | 934900 | 56094 | 0.06 | 0 | 57049.7 | 513447 | 0.45 | 376528 | 0.33 |  | 378810 | 0.332 |  | 2409779 | 2409779 | 0 | 120488.95 | 401258 | 162782 | 2.5 | 0.013999 |  |  | 7000 | 47464 | 54464 | 2100 | 45640 | 299054 | 401258 | 7000 | 47464 | 54464 | 2100 | 45640 | 299054 | 401258 | 401258 | 0 |  | 162782 | 156377.5688 | 1 | 934900 | 100000 | 50000 | 56094 | 1140994 | 57049.7 | 513447.3 | 376528.02 |  | 228198.8 | 228198.8 |  |  |  |  | 2259168.12 |  |  | 2259168.12 | stk added + 6% | 112958.406 |  |  | 7000 | 241.3793 | 47464 | 6.1363 | 54464 | 1 | 2100 | 90366.7248 | 92466.7248 | 146930.7248 | 54464 | 0.15121 | 92466.7248 | 0.25672 | 146930.7248 | 0.40794 | 1 | 213249.4886 | 360180.2134 | 401258 | 0.10237 | stk added + 10% |  |  | 144072.0854 | 140368.8053 | 20 | HPWI | 2259168.12 | 2259168.12 |  |  |  | 997500 | 1725675 | 1725675 |  |  |  | 1725675 | 1 | 39 | 9750 | 2.566 |  |  |  | 13638.8434 | 9547.1904 | 19.074 | 756.912 |  |  | 619.7454 |  |  | 1376.6574 | 4091.3808 | 252.38 | 4343.7608 |  | 4343.7608 | 5720.4181 | 68250 | 9750 | 78000 | 2606.2565 | 69027 | 1 | 148081.0643 | 219714.3208 | 225434.7389 |  | 90173.8956 | 87856.0337
8300-02 | NRG | CC10 |  |  |  |  | 1: 31; 2: 14; 6: 8300-02; 7: Cos Cob; 8: CC10; 9: 3; 11: 20; 12: 100; 13: Combustion Turbine; 14: Pratt & Whitney; 15: FT4-A9; 16: FT; 17: 1969; 18: 57 yrs; 19: Ultra low sulfur kerosene oil (ULSD); 21: 0.192; 23: 0.22; 34: 0; 35: 0.22; 38: CAIR-OS (max last 3 yrs); 39: 51; 40: 12848; 41: 0.19; 43: 1.2463; 49: 1 - Std; 50: Data not provided - per NRG no additional NOx controls are feasible.
8300-03 | NRG | CC11 |  |  |  |  | 1: 32; 2: 15; 6: 8300-03; 8: CC11; 9: 3; 11: 20; 13: Combustion Turbine; 14: Pratt & Whitney; 15: FT4-A9; 16: FT; 17: 1969; 18: 57 yrs; 19: Ultra low sulfur kerosene oil (ULSD); 21: 0.185; 23: 0.22; 34: 0; 35: 0.22; 38: CAIR-OS (max last 3 yrs); 43: 0; 49: 1 - Std
8300-04 | NRG | CC12 |  |  |  |  | 1: 33; 2: 16; 6: 8300-04; 8: CC12; 9: 3; 11: 20; 13: Combustion Turbine; 14: Pratt & Whitney; 15: FT4-A9; 16: FT; 17: 1969; 18: 57 yrs; 19: Ultra low sulfur kerosene oil (ULSD); 21: 0.194; 23: 0.22; 34: 0; 35: 0.22; 38: CAIR-OS (max last 3 yrs); 43: 0; 49: 1 - Std
8300-05 | NRG | CC13 |  |  |  |  | 1: 34; 2: 17; 6: 8300-05; 8: CC13; 9: 2; 11: 20; 13: Combustion Turbine; 14: Pratt & Whitney; 15: FT4-A9; 16: FT; 17: 1969; 18: 57 yrs; 19: Ultra low sulfur kerosene oil (ULSD); 20: Natural Gas; 21: 0.194; 23: 0.22; 34: 0; 35: 0.22; 38: CAIR-OS (max last 3 yrs); 39: 35; 40: 10832; 41: 0.19; 43: 1.0507; 49: 1 - Std
8300-06 | NRG | CC14 |  |  |  |  | 1: 35; 2: 18; 6: 8300-06; 8: CC14; 9: 2; 11: 20; 13: Combustion Turbine; 14: Pratt & Whitney; 15: FT4-A9; 16: FT; 17: 1969; 18: 57 yrs; 19: Ultra low sulfur kerosene oil (ULSD); 20: Natural Gas; 21: 0.171; 23: 0.22; 34: 0; 35: 0.22; 38: CAIR-OS (max last 3 yrs); 43: 0; 49: 1 - Std
8300-07 | NRG | FD10 | 8300-07-01 | High Pressure Water Injection (HPWI) | HPWI |  | 36 | 19 |  |  |  | 8300-07 | Franklin Drive | FD10 | 1 |  | 20 | 20 | Combustion Turbine | Pratt & Whitney | FT4-A8 | FT | Jan 1969 | 58 yrs | Ultra low sulfur kerosene oil (ULSD) |  | 0.76 |  | 0.8 |  | 48 hrs/year operation | [5 empty] | 2010-2009 average | 38.8 | 9915 | 9915 | 0.8 |  | 4.2 | CAIR-OS (max last 3 yrs) | 46 | 11515 | 0.76 |  | 4.3757 |  | 8300-07-01 | 1 | High Pressure Water Injection (HPWI) | HPWI | 1 - Std |  | 48 hrs/year operation | Cost Analysis not provided | [9 empty] | 2010-2009 average | Controlled NOx stk's rate is COS-COB units FLER | 0.22 |  | 1.2 | 1.2 | 1.0906 |  |  | 3 | 0.71429 | 0.725 | 0.725 | CAIR OS - max within last 3 yrs | Controlled NOx selected rate is COS-COB units max. last 3-yr stack rate | 103 | 0.209 |  | 1.2033 | 3.1724 | 0.725 | 0.725 | 0.725 |  | High Pressure Water Injection (HPWI) |  | 2409779 | 1140994 | 360000 | 159400 | 40000 | 250000 |  | 109500 |  | 16000 |  | 50000 |  |  | 100000 |  | 934900 | 56094 | [17 empty] | 1140994 | 1 | 1140994 |  |  | 513447 | 513447 |  |  |  | 376528 |  |  |  | 376528 |  |  |  | 378810 |  |  |  |  | 2409779 |  |  | 2409779 | 1140994 | 360000 | 0.31551 | 558900 | 0.48984 | 0 | 0 | 918900 | 0.80535 | 16000 | 0.014023 | 50000 | 0.043821 | 100000 | 0.087643 | 934900 | 56094 | 0.06 | 0 | 57049.7 | 513447 | 0.45 | 376528 | 0.33 |  | 378810 | 0.332 |  | 2409779 | 2409779 | 0 | 120488.95 | 401448 | 131838 | 3 | -0.015003 |  |  | 7000 | 47654.5 | 54654.5 | 2100 | 45639.5 | 299054 | 401448 | 7000 | 47654.5 | 54654.5 | 2100 | 45639.5 | 299054 | 401448 | 401448 | 0 |  | 131838 | 126544.6396 | 1 | 934900 | 100000 | 50000 | 56094 | 1140994 | 57049.7 | 513447.3 | 376528.02 |  | 228198.8 | 228198.8 |  |  |  |  | 2259168.12 |  |  | 2259168.12 | stk added + 6% | 112958.406 |  |  | 7000 | 180.4124 | 47654.5 | 4.8063 | 54654.5 | 1 | 2100 | 90366.7248 | 92466.7248 | 147121.2248 | 54654.5 | 0.15166 | 92466.7248 | 0.25659 | 147121.2248 | 0.40825 | 1 | 213249.4886 | 360370.7134 | 401448 | 0.10232 | stk added + 10% |  |  | 120123.5711 | 113596.2367 | 20 | HPWI | 2259168.12 | 2259168.12 |  |  |  | 997500 | 1725675 | 1725675 |  |  |  | 1725675 | 1 | 46 | 11515 | 3.1724 |  |  |  | 13656.6332 | 9559.6433 | 19.0989 | 892.768 |  |  | 731.9352 |  |  | 1624.7032 | 4825.7312 | 297.6789 | 5123.4101 |  | 5123.4101 | 6748.1133 | 80605 | 11500 | 92105 | 3074.0461 | 69027 | 1 | 148081.0643 | 220182.1104 | 226930.2237 |  | 75643.4079 | 71533.0587
8300-08 | NRG | TT10 | 8300-08-01 | High Pressure Water Injection (HPWI) | HPWI |  | 37 | 20 |  |  |  | 8300-08 | Torrington Terminal | TT10 | 1 |  | 20 | 20 | Combustion Turbine | Pratt & Whitney | FT4-A8 | FT | Jan 1969 | 58 yrs | Ultra low sulfur kerosene oil (ULSD) |  | 0.68 |  | 0.8 |  | 48 hrs/year operation | [5 empty] | 2010-2009 average | 29.5 | 8325 | 8325 | 0.8 |  | 3.2 | CAIR-OS (max last 3 yrs) | 36 | 9070 | 0.68 |  | 3.0838 |  | 8300-08-01 | 1 | High Pressure Water Injection (HPWI) | HPWI | 1 - Std |  | 48 hrs/year operation | Cost Analysis not provided | [9 empty] | 2010-2009 average | Controlled NOx stk's rate is COS-COB units FLER | 0.22 |  | 0.9 | 0.9 | 0.91575 |  |  | 2.3 | 0.71875 | 0.725 | 0.725 | CAIR OS - max within last 3 yrs | Controlled NOx selected rate is COS-COB units max. last 3-yr stack rate | 103 | 0.187 |  | 0.84805 | 2.2358 | 0.725 | 0.725 | 0.725 |  | High Pressure Water Injection (HPWI) |  | 2409779 | 1140994 | 360000 | 159400 | 40000 | 250000 |  | 109500 |  | 16000 |  | 50000 |  |  | 100000 |  | 934900 | 56094 | [17 empty] | 1140994 | 1 | 1140994 |  |  | 513447 | 513447 |  |  |  | 376528 |  |  |  | 376528 |  |  |  | 378810 |  |  |  |  | 2409779 |  |  | 2409779 | 1140994 | 360000 | 0.31551 | 558900 | 0.48984 | 0 | 0 | 918900 | 0.80535 | 16000 | 0.014023 | 50000 | 0.043821 | 100000 | 0.087643 | 934900 | 56094 | 0.06 | 0 | 57049.7 | 513447 | 0.45 | 376528 | 0.33 |  | 378810 | 0.332 |  | 2409779 | 2409779 | 0 | 120488.95 | 401268.5 | 172961 | 2.3 | -0.0086931 |  |  | 7000 | 47475 | 54475 | 2100 | 45639.5 | 299054 | 401268.5 | 7000 | 47475 | 54475 | 2100 | 45639.5 | 299054 | 401268.5 | 401268.5 | 0 |  | 172961 | 179477.8498 | 1 | 934900 | 100000 | 50000 | 56094 | 1140994 | 57049.7 | 513447.3 | 376528.02 |  | 228198.8 | 228198.8 |  |  |  |  | 2259168.12 |  |  | 2259168.12 | stk added + 6% | 112958.406 |  |  | 7000 | 237.2881 | 47475 | 5.7027 | 54475 | 1 | 2100 | 90366.7248 | 92466.7248 | 146941.7248 | 54475 | 0.15124 | 92466.7248 | 0.25672 | 146941.7248 | 0.40795 | 1 | 213249.4886 | 360191.2134 | 401268.5 | 0.10237 | stk added + 10% |  |  | 156604.8754 | 161104.9571 | 20 | HPWI | 2259168.12 | 2259168.12 |  |  |  | 997500 | 1725675 | 1725675 |  |  |  | 1725675 | 1 | 36 | 9070 | 2.2358 |  |  |  | 13744.9233 | 9621.4463 | 19.2223 | 698.688 |  |  | 576.5221 |  |  | 1275.2101 | 3776.6592 | 232.9661 | 4009.6253 |  | 4009.6253 | 5284.8354 | 63490 | 9000 | 72490 | 2405.7752 | 69027 | 1 | 148081.0643 | 219513.8395 | 224798.6749 |  | 97738.5543 | 100547.097
8300-09 | NRG | MD10 | 8300-09-01 | High Pressure Water Injection (HPWI) | HPWI |  | 38 | 21 |  |  |  | 8300-09 | Middletown | MD10 | 1 |  | 20 | 953 | Combustion Turbine | Pratt & Whitney | FT4-A8 | FT | Aug 1966 | 60 yrs | Ultra low sulfur kerosene oil (ULSD) |  | 0.57 |  | 0.67 |  | 48 hrs/year operation | [5 empty] | 2010-2009 average | 99.9 | 20980 | 20980 | 0.67 |  | 6.2 | CAIR-OS (max last 3 yrs) | 95 | 23750 | 0.57 |  | 6.7687 |  | 8300-09-01 | 1 | High Pressure Water Injection (HPWI) | HPWI | 1 - Std |  | 48 hrs/year operation | Cost Analysis not provided | [9 empty] | 2010-2009 average | Controlled NOx stk's rate is COS-COB units FLER | 0.22 |  | 2 | 2 | 2.3078 |  |  | 4.2 | 0.67742 | 0.67164 | 0.67164 | CAIR OS - max within last 3 yrs | Controlled NOx selected rate is COS-COB units max. last 3-yr stack rate | 103 | 0.18716 |  | 2.2226 | 4.5462 | 0.67164 | 0.67164 | 0.67164 |  | High Pressure Water Injection (HPWI) |  | 2304179 | 1090994 | 360000 | 159400 | 40000 | 250000 |  | 109500 |  | 16000 |  |  |  |  | 100000 |  | 934900 | 56094 | [17 empty] | 1090994 | 1 | 1090994 |  |  | 490947 | 490947 |  |  |  | 360028 |  |  |  | 360028 |  |  |  | 362210 |  |  |  |  | 2304179 |  |  | 2304179 | 1090994 | 360000 | 0.32997 | 558900 | 0.51229 | 0 | 0 | 918900 | 0.84226 | 16000 | 0.014666 | 0 | 0 | 100000 | 0.09166 | 934900 | 56094 | 0.06 | 0 | 54549.7 | 490947 | 0.45 | 360028 | 0.33 |  | 362210 | 0.332 |  | 2304179 | 2304179 | 0 | 115208.95 | 386561 | 92830 | 4.2 | 0.0085281 |  |  | 7000 | 47872.5 | 54872.5 | 2100 | 43639.5 | 285949 | 386561 | 7000 | 47872.5 | 54872.5 | 2100 | 43639.5 | 285949 | 386561 | 386561 | 0 |  | 92830 | 85029.9358 | 1 | 934900 | 100000 | 0 | 56094 | 1090994 | 54549.7 | 490947.3 | 360028.02 |  | 218198.8 | 218198.8 |  |  |  |  | 2160168.12 |  |  | 2160168.12 | stk added + 6% | 108008.406 |  |  | 7000 | 70.0701 | 47872.5 | 2.2818 | 54872.5 | 1 | 2100 | 86406.7248 | 88506.7248 | 143379.2248 | 54872.5 | 0.158 | 88506.7248 | 0.25485 | 143379.2248 | 0.41286 | 1 | 203904.5889 | 347283.8137 | 386561 | 0.10161 | stk added + 10% |  |  | 82686.6223 | 76390.3249 | 20 | HPWI | 2160168.12 | 2160168.12 |  |  |  | 997500 | 1725675 | 1725675 |  |  |  | 1725675 | 1 | 95 | 23750 | 4.5462 |  |  |  | 13638.8434 | 9547.1904 | 19.074 | 1843.76 |  |  | 1509.6361 |  |  | 3353.3961 | 9966.184 | 614.7717 | 10580.9557 |  | 10580.9557 | 13934.3518 | 166250 | 23750 | 190000 | 6348.5734 | 69027 | 1 | 148081.0643 | 223456.6377 | 237390.9896 |  | 56521.6642 | 52217.7369
8300-10 | NRG | NH10 | 8300-10-01 | High Pressure Water Injection (HPWI) | HPWI |  | 39 | 22 |  |  |  | 8300-10 | Norwalk Harbor Station | NH10 | 1 |  | 17 | 353 | Combustion Turbine | Westinghouse | W191 |  | Oct 1966 | 60 yrs | No.2 Oil |  | 0.514 |  | 0.52 |  | 48 hrs/year operation | [5 empty] | 2010-2009 average | 14.5 | 3480 | 3480 | 0.52 |  | 1 | CAIR-OS (max last 3 yrs) | 21 | 4848.2609 | 0.51 |  | 1.246 |  | 8300-10-01 | 1 | High Pressure Water Injection (HPWI) | HPWI | 1 - Std |  | 48 hrs/year operation | Cost Analysis not provided | [9 empty] | 2010-2009 average | Controlled NOx stk's rate is COS-COB units FLER | 0.26 |  | 0.5 | 0.5 | 0.4524 |  |  | 0.5 | 0.5 | 0.5 | 0.5 | CAIR OS - max within last 3 yrs | Controlled NOx selected rate is COS-COB units max. last 3-yr stack rate | 103 | 0.257 |  | 0.623 | 0.623 | 0.5 | 0.49608 | 0.5 |  | High Pressure Water Injection (HPWI) |  | 1592321 | 753940 | 360000 | 25000 | 15000 | 100000 |  | 89500 |  | 16000 |  |  |  |  | 100000 |  | 605500 | 48440 | [17 empty] | 753940 | 1 | 753940 |  |  | 339273 | 339273 |  |  |  | 248800 |  |  |  | 248800 |  |  |  | 250308 |  |  |  |  | 1592321 |  |  | 1592321 | 753940 | 360000 | 0.47749 | 229500 | 0.3044 | 0 | 0 | 589500 | 0.78189 | 16000 | 0.021222 | 0 | 0 | 100000 | 0.13264 | 605500 | 48440 | 0.08 | 0 | 44349.4118 | 339273 | 0.45 | 248800 | 0.33 |  | 250308 | 0.332 |  | 1592321 | 1592321 | 0 | 93665.9412 | 495392 | 990785 | 0.5 | 1.0093e-06 |  |  | 7000 | 46760.5 | 53760.5 | 2100 | 30157.5 | 409374 | 495392 | 7000 | 46760.5 | 53760.5 | 2100 | 30157.5 | 409374 | 495392 | 495392 | 0 |  | 990785 | 795169.8073 | 1 | 605500 | 100000 | 0 | 36330 | 741830 | 43637.0588 | 333823.5 | 244803.9 |  | 148366 | 148366 |  |  |  |  | 1468823.4 |  |  | 1468823.4 | stk added + 8% | 86401.3765 |  |  | 7000 | 482.7586 | 46760.5 | 13.4369 | 53760.5 | 1 | 2100 | 58752.936 | 60852.936 | 114613.436 | 53760.5 | 0.21227 | 60852.936 | 0.24028 | 114613.436 | 0.45255 | 1 | 138646.5381 | 253259.9741 | 495392 | 0.48877 | stk added + 49% | Stakholder reported an large CR of $409374 hence Annual Costs of $495392 |  | 506519.9483 | 406515.8194 | 17 | HPWI | 1468823.4 | 1468823.4 |  |  |  | 891600 | 1542468 | 1542468 |  |  |  | 1542468 | 1 | 21 | 4848.2609 | 0.623 |  |  |  | 12595.1754 | 8816.6228 | 17.6144 | 407.568 |  |  | 308.173 |  |  | 715.741 | 2203.0512 | 121.4694 | 2324.5206 |  | 2324.5206 | 3040.2616 | 33937.8261 | 5250 | 39187.8261 | 1394.7123 | 61698.72 | 1 | 132359.9769 | 195453.4092 | 198493.6708 |  | 396987.3416 | 318608.6452
8300-11 | NRG | DV10 | 8300-11-01 | Selective Catalytic Reduction (SCR) | SCR |  | 40 | 23 |  |  |  | 8300-11 | Devon | DV10 | 1 |  | 20 | 180 | Combustion Turbine | Pratt & Whitney | FT4-A8 | FT | Mar 1988 | 38 yrs | Ultra low sulfur kerosene oil (ULSD) |  | 0.67 |  | 0.74 |  | 48 hrs/year operation | [5 empty] | 2010-2009 average | 20.55 | 4855 | 4855 | 0.74 |  | 1.8 | CAIR-OS (max last 3 yrs) | 24 | 5575 | 0.67 |  | 1.8676 |  | 8300-11-01 | 1 | Selective Catalytic Reduction (SCR) | SCR | 1 - Std |  | 48 hrs/year operation | Cost Analysis not provided | [9 empty] | 2010-2009 average | Controlled NOx rate was assessed by stakeholder | 0.1 |  | 0.24 | 0.24 | 0.24275 |  |  | 1.56 | 0.86667 | 0.86486 | 0.9 | CAIR OS - max within last 3 yrs | Controlled NOx rate was calculated assuming 90% efficiency | 106 | 0.067 |  | 0.18676 | 1.6809 | 0.9 | 0.9 | 0.9 | 0.9 | Selective Catalytic Reduction (SCR) |  | 6494100 | 3074858 | 1367375 | 625000 | 125000 | 300000 |  |  |  | 200000 |  |  |  | 183434 | 100000 |  | 2800809 | 174049 | [17 empty] | 3074858 | 1 | 3074858 |  |  | 1383686 | 1383686 |  |  |  | 1014703 |  |  |  | 1014703 |  |  |  | 1020853 |  |  |  |  | 6494100 |  |  | 6494100 | 3074858 | 1367375 | 0.4447 | 1050000 | 0.34148 | 0 | 0 | 2417375 | 0.78617 | 200000 | 0.065044 | 0 | 0 | 100000 | 0.032522 | 2800809 | 174049 | 0.062142 | 0 | 153742.9 | 1383686 | 0.45 | 1014703 | 0.33 |  | 1020853 | 0.332 |  | 6494100 | 6494100 | 0 | 324705 | 938619 | 602932 | 1.56 | 0.0020784 |  |  | 0 | 9974 | 9974 | 0 | 122994 | 805651 | 938619 | 0 | 9974 | 9974 | 0 | 122994 | 805651 | 938619 | 938619 | 0 |  | 602932 | 558415.0994 | 1 | 2800809 | 100000 | 0 | 168048.54 | 3068857.54 | 153442.877 | 1380985.893 | 1012722.9882 |  | 613771.508 | 613771.508 |  |  |  |  | 6076337.9292 |  |  | 6076337.9292 | stk added + 6% | 303816.8965 |  |  | 0 |  | 9974 | 2.0544 | 9974 | 1 | 0 | 243053.5172 | 243053.5172 | 253027.5172 | 9974 | 0.012066 | 243053.5172 | 0.29404 | 253027.5172 | 0.30611 | 1 | 573563.3149 | 826590.8321 | 938619 | 0.11935 | stk added + 12% |  |  | 529865.918 | 491765.8834 | 20 | SCR | 6076337.9292 | 6076337.9292 |  |  |  | 1453000 | 2513690 | 2513690 |  |  |  | 2513690 | 2 | 24 | 5575 | 1.6809 | 1000 | 0.07 | 1489.1566 |  |  |  | 1018.656 | 1046.8412 | 701.9994 | 2705.053 | 931.584 | 93.1584 | 6497.2919 | 2517.7728 | 226.2321 | 2744.0049 |  | 2744.0049 | 9241.2968 | 1672.5 | 16813.76 | 18486.26 | 1646.4029 | 100547.6 | 1 | 215701.039 | 317895.042 | 327136.3388 |  | 209702.7813 | 194624.0926
|  |  | 8300-11-02 | High Pressure Water Injection (HPWI) | HPWI |  | 1: 41; 33: #N/A; 45: 8300-11-02; 46: 2; 47: High Pressure Water Injection (HPWI); 48: HPWI; 49: 1 - Std; 51: 48 hrs/year operation; 52: Cost Analysis not provided; 62: 2010-2009 average; 63: Controlled NOx stk's rate is COS-COB units FLER; 64: 0.22; 66: 0.5; 67: 0.5; 68: 0.53405; 71: 1.3; 72: 0.72222; 73: 0.7027; 74: 0.7027; 75: CAIR OS - max within last 3 yrs; 76: Controlled NOx selected rate is COS-COB units max. last 3-yr stack rate; 77: 103; 78: 0.19919; 80: 0.55524; 81: 1.3124; 82: 0.7027; 83: 0.7027; 84: 0.7027; 86: High Pressure Water Injection (HPWI); 88: 1800457; 89: 852494; 90: 360000; 91: 134400; 92: 40000; 93: 50000; 95: 109500; 97: 16000; 102: 100000; 104: 709900; 105: 42594; 123: 852494; 124: 1; 125: 852494; 128: 383622; 129: 383622; 133: 281323; 137: 281323; 141: 283028; 146: 1800467; 149: 1800467; 150: 852494; 151: 360000; 152: 0.42229; 153: 333900; 154: 0.39167; 155: 0; 156: 0; 157: 693900; 158: 0.81396; 159: 16000; 160: 0.018768; 161: 0; 162: 0; 163: 100000; 164: 0.1173; 165: 709900; 166: 42594; 167: 0.06; 168: 0; 169: 42624.7; 170: 383622; 171: 0.45; 172: 281323; 173: 0.33; 175: 283028; 176: 0.332; 178: 1800467; 179: 1800467; 180: 5.5541e-06; 181: 90023.35; 182: 313560; 183: 247900; 184: 1.3; 185: 0.027027; 188: 7000; 189: 46922.5; 190: 53922.5; 191: 2100; 192: 34099.5; 193: 223438; 194: 313560; 195: 7000; 196: 46922.5; 197: 53922.5; 198: 2100; 199: 34099.5; 200: 223438; 201: 313560; 202: 313560; 203: 0; 205: 247900; 206: 238923.7668; 207: 1; 208: 709900; 209: 100000; 210: 0; 211: 42594; 212: 852494; 213: 42624.7; 214: 383622.3; 215: 281323.02; 217: 170498.8; 218: 170498.8; 223: 1687938.12; 226: 1687938.12; 227: stk added + 6%; 228: 84396.906; 231: 7000; 232: 340.6326; 233: 46922.5; 234: 9.6648; 235: 53922.5; 236: 1; 237: 2100; 238: 67517.5248; 239: 69617.5248; 240: 123540.0248; 241: 53922.5; 242: 0.19063; 243: 69617.5248; 244: 0.24611; 245: 123540.0248; 246: 0.43674; 247: 1; 248: 159329.4176; 249: 282869.4424; 250: 313560; 251: 0.097878; 252: stk added + 10%; 255: 217591.8788; 256: 215538.4383; 257: 20; 258: HPWI; 259: 1687938.12; 260: 1687938.12; 264: 997500; 265: 1725675; 266: 1725675; 270: 1725675; 271: 1; 272: 24; 273: 5575; 274: 1.3124; 278: 12672.7587; 279: 8870.9311; 280: 17.7229; 281: 465.792; 284: 354.3672; 287: 820.1592; 288: 2517.7728; 289: 155.3108; 290: 2673.0835; 292: 2673.0835; 293: 3493.2428; 294: 39025; 295: 6000; 296: 45025; 297: 1603.8501; 298: 69027; 299: 1; 300: 148081.0643; 301: 218711.9144; 302: 222205.1572; 304: 170927.044; 305: 169313.9851
8300-12 | NRG | DV11 | 8300-12-01 | Selective Catalytic Reduction (SCR) | SCR |  | 42 | 24 |  |  |  | 8300-12 |  | DV11 | 4 |  | 40 |  | Combustion Turbine | General Electric | LM6000PA |  | Jun 1996 | 30 yrs | ULSD oil | Natural Gas | 0.171 |  | 0.171 |  | 48 hrs/year operation | [5 empty] | 2010-2009 average | 80.7 | 125150 | 31287.5 | 0.171 |  | 2.66 | CAIR-OS (max last 3 yrs) | 96 | 30042 | 0.15 |  | 2.3 |  | 8300-12-01 | 1 | Selective Catalytic Reduction (SCR) | SCR | 1 - Std |  | 48 hrs/year operation | Cost Analysis not provided | [9 empty] | 2010-2009 average | Controlled NOx rate was assessed by stakeholder | 0.05 |  | 3.13 | 0.7825 | 0.78219 |  |  | 1.8775 | 0.70583 | 0.7076 | 0.9 | CAIR OS - max within last 3 yrs | Controlled NOx rate was calculated assuming 90% efficiency | 106 | 0.015312 |  | 0.23 | 2.07 | 0.9 | 0.89792 | 0.9 | 0.9 | Selective Catalytic Reduction (SCR) |  | 45848986 | 21708800 | 10939000 | 1791000 | 2000000 | 1500000 | 100000 |  |  | 4000000 |  |  |  |  | 150000 |  | 20330000 | 1228800 | [17 empty] | 21708800 | 1 | 21708800 |  |  | 9768960 | 9768960 |  |  |  | 7163904 |  |  |  | 7163904 |  |  |  | 7207322 |  |  |  |  | 45848986 |  |  | 45848986 | 5427200 | 2734750 | 0.5039 | 1347750 | 0.24833 | 0 | 0 | 4082500 | 0.75223 | 1000000 | 0.18426 | 0 | 0 | 37500 | 0.0069096 | 5082500 | 307200 | 0.060443 | 0 | 135680 | 2442240 | 0.45 | 1790976 | 0.33 |  | 1801830.5 | 0.332 |  | 11462246.5 | 11462246.5 | 0 | 286556.1625 | 3588382 | 477897 | 7.51 | 0.000174 |  |  | 0 | 25968 | 25968 | 0 | 868352 | 2694062 | 3588382 | 0 | 6492 | 6492 | 0 | 217088 | 673515.5 | 897095.5 | 897095.5 | 0 |  | 477897 | 433379.4686 | 1 | 5082500 | 37500 | 0 | 304950 | 5424950 | 135623.75 | 2441227.5 | 1790233.5 |  | 1084990 | 1084990 |  |  |  |  | 10741401 |  |  | 10741401 | stk added + 6% | 268535.025 |  |  | 0 |  | 25968 | 0.82998 | 25968 | 1 | 0 | 429656.04 | 429656.04 | 455624.04 | 6492 | 0.0057562 | 107414.01 | 0.095241 | 113906.01 | 0.101 | 1 | 1013912.267 | 1127818.277 | 897095.5 | -0.25719 | -0.25719 | Stakholder reported a lower Capital Recovery than 9%/15 yrs |  | 600702.1449 | 544839.7473 | 40 | SCR | 10741401 | 10741401 |  |  |  | 2447000 | 4233310 | 4233310 |  |  |  | 4233310 | 2 | 96 | 30042 | 2.07 | 250 | 0.07 | 2978.3133 |  |  |  | 4074.624 | 1289.196 | 864.5197 | 5410.1063 | 7452.672 | 745.2672 | 19836.3851 | 10071.0912 | 1523.9916 | 11595.0828 |  | 11595.0828 | 31431.4679 | 9012.6 | 18501.5018 | 27514.1018 | 6957.0497 | 169332.4 | 1 | 363262.5207 | 539551.9703 | 570983.4383 |  | 304119.0084 | 275837.4098
8300-13 | NRG | DV12 |  |  |  |  | 1: 43; 2: 25; 6: 8300-13; 8: DV12; 9: 4; 11: 40; 13: Combustion Turbine; 14: General Electric; 15: LM6000PA; 17: Jun 1996; 18: 30 yrs; 19: ULSD oil; 20: Natural Gas; 21: 0.171; 23: 0.171; 25: 48 hrs/year operation; 31: 2010-2009 average; 32: 65.3; 34: 31287.5; 35: 0.171; 37: 2.66; 38: CAIR-OS (max last 3 yrs); 49: 1 - Std; 236: 1
8300-14 | NRG | DV13 |  |  |  |  | 1: 44; 2: 26; 6: 8300-14; 8: DV13; 9: 4; 11: 40; 13: Combustion Turbine; 14: General Electric; 15: LM6000PA; 17: Jun 1996; 18: 30 yrs; 19: ULSD oil; 20: Natural Gas; 21: 0.171; 23: 0.171; 25: 48 hrs/year operation; 31: 2010-2009 average; 32: 94.5; 34: 31287.5; 35: 0.171; 37: 2.66; 38: CAIR-OS (max last 3 yrs); 49: 1 - Std; 236: 1
8300-15 | NRG | DV14 |  |  |  |  | 1: 45; 2: 27; 6: 8300-15; 8: DV14; 9: 4; 11: 40; 13: Combustion Turbine; 14: General Electric; 15: LM6000PA; 17: Jun 1996; 18: 30 yrs; 19: ULSD oil; 20: Natural Gas; 21: 0.171; 23: 0.171; 25: 48 hrs/year operation; 31: 2010-2009 average; 32: 101.4; 34: 31287.5; 35: 0.171; 37: 2.66; 38: CAIR-OS (max last 3 yrs); 49: 1 - Std; 64: 0.933; 236: 1
8300-16 | NRG | MV10 | 8300-16-01 | Selective Catalytic Reduction (SCR) | SCR |  | 46 | 1 | 6 | NRG Energy, Inc |  | 8300-16 | Montville | MV10 | 2 |  | 2.75 | 488.5 | Diesel Engine | General Motors | EMD 20-645-E4 |  | Jan 1966 | 61 yrs | 0.05% sulfur distillate oil |  | 3.09 |  | 3.11 |  | 48 hrs/year operation | [5 empty] | 2010-2009 average | 235.95 |  |  | 3.11 |  | 6 | CAIR-OS (max last 3 yrs) | 316.2 |  |  |  | 14.1673 |  | 8300-16-01 | 1 | Selective Catalytic Reduction (SCR) | SCR | 1 - Std |  | 48 hrs/year operation | Cost Analysis not provided | [9 empty] | 2010-2009 average | Controlled NOx rate was assessed by stakeholder | 0.933 |  | 3.6 | 1.8 | 14.5956 |  |  | 4.2 | 0.7 | 0.7 | 0.9 | CAIR OS - max within last 3 yrs | Controlled NOx (R) was calculated assuming 90% efficiency | HI is not known | 0.311 |  | 1.4167 | 12.7506 | 0.9 |  | 0.9 | 0.9 | Selective Catalytic Reduction (SCR) |  | 1129075 | 1069200 | 600000 | 20000 | 20000 | 20000 |  | 20000 |  | 140000 |  |  |  |  | 200000 |  | 820000 | 49200 | [17 empty] | 1069200 | 1 | 1069200 |  |  | 481140 | 481140 |  |  |  | 352836 |  |  |  | 352836 |  |  |  | 354974 |  |  |  |  | 2258150 |  |  | 2258150 | 534600 | 300000 | 0.56117 | 40000 | 0.074822 | 0 | 0 | 340000 | 0.63599 | 70000 | 0.13094 | 0 | 0 | 100000 | 0.18706 | 410000 | 24600 | 0.06 | 0 | 194400 | 240570 | 0.45 | 176418 | 0.33 |  | 177487 | 0.332 |  | 1129075 | 1129075 | 0.5 | 410572.7273 | 666775 | 79606 | 8.4 | 0.0028644 |  |  | 20000 | 17453 | 37453 | 6000 | 42768 | 580554 | 666775 | 10000 | 8726.5 | 18726.5 | 3000 | 21384 | 290277 | 333387.5 | 333387.5 | 0 |  | 79606 | 26146.7946 | 1 | 410000 | 100000 | 0 | 24600 | 534600 | 194400 | 240570 | 176418 |  | 106920 | 106920 |  |  |  |  | 1058508 |  |  | 1058508 | stk added + 6% | 384912 |  |  | 20000 | 84.7637 | 17453 |  | 37453 | 1 | 6000 | 42340.32 | 48340.32 | 85793.32 | 18726.5 | 0.13113 | 24170.16 | 0.16924 | 42896.66 | 0.30037 | 1 | 99915.667 | 142812.327 | 333387.5 | 0.57163 | stk added + 57% | Stakholder reported an large CR of $290277 hence Annual Costs of $333387.5 |  | 34002.935 | 11200.4337 | 2.75 | SCR | 1058508 | 1058508 |  |  |  | 595675 | 1030517.75 | 1030517.75 |  |  |  | 1030517.75 | 2 | 316.2 | 2065.3875 | 12.7506 | 75.9013 | 0.070414 | 204.759 |  |  |  | 13420.7928 | 7941.078 | 5325.1935 | 374.1466 | 1687.6226 | 168.7623 | 28917.5957 | 33171.6566 | 1221.9364 | 34393.5931 |  | 34393.5931 | 63311.1888 | 619.6163 | 20087.5808 | 20707.197 | 20636.1558 | 41220.71 | 1 | 88429.2611 | 150286.127 | 213597.3157 |  | 50856.5037 | 16751.9333
8300-17 | NRG | MV11 |  |  |  |  | 1: 47; 2: 2; 6: 8300-17; 8: MV11; 9: 2; 11: 2.75; 13: Diesel Engine; 14: General Motors; 15: EMD 20-645-E4; 17: Jan 1966; 18: 61 yrs; 19: 0.05% sulfur distillate oil; 21: 1.93; 23: 2.96; 25: 48 hrs/year operation; 31: 2010-2009 average; 32: 148.5; 35: 2.96; 37: 6; 38: CAIR-OS (max last 3 yrs); 39: 113.5; 49: 1 - Std; 207: 1; 236: 1; 272: MW10-11 Heat Input is estimate from DV11-14
8306-01 | NRG | MD2 | 8306-01-01 | Rotating Opposed Fire Air (ROFA) | New Eqp |  | 48 | 1 | 6 |  | 8306 | 8306-01 | Middletown | MD2 | 1 |  | 120 | 953 | Utility Boiler | Riley | Front fired |  |  |  | No. 6 oil | No. 2 oil |  |  | 0.18 |  | 48 hrs/year operation | [5 empty] | 2010-2009 average | 1331.1 | 1017740 | 1017740 | 0.18 |  | 91.6 | CAIR-OS (max last 3 yrs) | 1670 | 1434563 | 0.13 |  | 94.2 |  | 8306-01-01 | 1 | Rotating Opposed Fire Air (ROFA) | New Eqp | 2 - Prog | [12 empty] | 2010-2009 average |  | 0.15 |  | 76.33 | 76.33 | 76.3305 |  |  | 15.27 | 0.1667 | 0.16667 | 0.35 | CAIR OS - max within last 3 yrs | For Utility Boilers Controlled NOx (R) was assumed 0.150 lbs/MMBtu |  | 0.085364 |  | 61.23 | 32.97 | 0.35 | 0.34335 | 0.35 | 0.35 | Rotating Opposed Fire Air (ROFA) |  | 6191539 | 3077275 | 2178750 | 0 | 530000 | 100000 | [8 empty] | 100000 |  | 2808750 | 168525 | [17 empty] | 3077275 | 1 | 3077275 |  |  | 1384773.6 | 1384773.6 | 223102.43 | 446204.86 | 223102.43 |  |  |  |  | 892409.72 |  |  |  | 803169 | 33911.5744 | 0 |  |  | 6157627.32 |  |  | 6157627.32 | 3077275 | 2178750 | 0.70801 | 630000 | 0.20473 | 0 | 0 | 2808750 | 0.91274 | 0 | 0 | 0 | 0 | 100000 | 0.032496 | 2808750 | 168525 | 0.06 | 0 | 25643.9583 | 1384773.6 | 0.45 | 892409.72 | 0.29 | 0.2 | 803169 | 0.261 | 0.15 | 6157627.32 | 6191538.8944 | -1.7056e-08 | 51596.1575 | 1764485 | 115582 | 15.27 | 0.00025618 |  |  | 25000 | 147687 | 172687 |  |  | 1591798 | 1764485 | 25000 | 147687 | 172687 |  |  | 1591798 | 1764485 | 1764485 | 0 |  | 115582 | 53517.8951 | 2 | 2808750 | 100000 | 0 | 168525 | 3077275 | 25643.9583 | 1384773.75 | 892409.75 |  | 803168.775 | 803168.775 | 33911.5705 | 0 |  |  | 6191538.8455 |  |  | 6191538.8455 | stk added + 0% | 51596.157 |  |  | 25000 | 18.7815 | 147687 | 0.14511 | 172687 | 0 | 0 | 0 |  | 172687 | 172687 | 0.27105 |  |  | 172687 | 0.27105 | 2 | 464421.9971 | 637108.9971 | 1764485 | 0.63893 | stk added + 64% |  |  | 41722.9206 | 19323.9004 | 120 | Other | 6191538.8455 | 6191538.8455 |  |  |  | N/A |  | 6191538.8455 |  |  |  | 6191538.8455 | 2 | 1670 | 1434563 | 32.97 | 14.3713 | 0.11258 | 8934.9398 |  |  |  | 70881.48 | 20533.716 | 13769.6684 | 26102.0291 | 388936.32 | 38893.632 | 559116.8455 | 175195.024 | 38774.512 | 213969.536 | 291698.9767 | 505668.5127 | 1064785.3582 | 430368.9 | 22531.8942 | 452900.7942 | 128381.7216 | 247661.5538 | 2 | 464421.9971 | 840465.2725 | 1905250.6308 |  | 124770.8337 | 57787.4016
|  |  | 8306-01-02 | Selective Catalytic Reduction (SCR) with ID fans | SCR |  | 1: 49; 33: #N/A; 45: 8306-01-02; 46: 2; 47: Selective Catalytic Reduction (SCR) with ID fans; 48: SCR; 49: 4 - Custom; 62: 2010-2009 average; 64: 0.1; 66: 50.89; 67: 50.89; 68: 50.887; 71: 40.71; 72: 0.44443; 73: 0.44444; 74: 0.9; 75: CAIR OS - max within last 3 yrs; 76: Controlled NOx rate was calculated assuming 90% efficiency; 78: 0.013133; 80: 9.42; 81: 84.78; 82: 0.9; 83: 0.89898; 84: 0.9; 85: 0.9; 86: Selective Catalytic Reduction (SCR) with ID fans; 88: 65903462; 89: 16190210; 90: 11205248; 91: 1047064; 92: 733549; 93: 1715272; 95: 615635; 97: 873442; 104: 16190210; 123: 16190210; 124: 1; 125: 16190210; 126: 371030; 127: 30607972; 129: 30979002; 134: 558479; 135: 13328721; 136: 4847050; 137: 18734250; 146: 65903462; 149: 65903462; 150: 16190210; 151: 11205248; 152: 0.6921; 153: 4111520; 154: 0.25395; 155: 0; 156: 0; 157: 15316768; 158: 0.94605; 159: 873442; 160: 0.053949; 161: 0; 162: 0; 163: 0; 164: 0; 165: 16190210; 168: 0; 169: 134918.4167; 170: 30979002; 171: 1.9134; 172: 18734250; 173: 1.1571; 174: 0.39717; 178: 65903462; 179: 65903462; 180: 0; 181: 549195.5167; 182: 17113676; 183: 420384; 184: 40.71; 185: 9.1528e-06; 188: 15000; 189: 155393; 190: 170393; 193: 16943283; 194: 17113676; 195: 15000; 196: 155393; 197: 170393; 200: 16943283; 201: 17113676; 202: 17113676; 203: 0; 205: 420384; 206: 201859.8254; 207: 4; 208: 16190210; 209: 0; 210: 0; 212: 16190210; 213: 134918.4167; 214: 30979002; 215: 18734250; 218: 0; 223: 65903462; 226: 65903462; 227: same TCC; 228: 549195.5167; 231: 15000; 232: 11.2689; 233: 155393; 234: 0.15268; 235: 170393; 236: 0; 237: 0; 238: 0; 240: 170393; 241: 170393; 242: 0.033321; 245: 170393; 246: 0.033321; 247: 2; 248: 4943361.9334; 249: 5113754.9334; 250: 17113676; 251: 0.70119; 252: stk added + 70%; 255: 125614.2209; 256: 60317.9398; 257: 120; 258: SCR; 259: 65903462; 260: 65903462; 264: 6423000; 265: 11111790; 266: 11111790; 270: 11111790; 271: 2; 272: 1670; 273: 1434563; 274: 84.78; 275: 14.3713; 276: 0.11258; 277: 8934.9398; 281: 70881.48; 282: 52800.984; 283: 35407.7187; 284: 26102.0291; 285: 388936.32; 286: 38893.632; 287: 613022.1638; 288: 175195.024; 289: 69587.5849; 290: 244782.6089; 291: 291698.9767; 292: 536481.5856; 293: 1149503.7494; 294: 430368.9; 295: 22531.8942; 296: 452900.7942; 297: 146869.5653; 298: 444471.6; 299: 2; 300: 833485.7992; 301: 1424826.9646; 302: 2574330.714; 304: 63235.8318; 305: 30364.835
[7 empty] | 50 | [234 empty] | 0
8306-02 | NRG | MD3 | 8306-02-01 | Separated Overfired Air / High Energy Reagent Technology (SOFA/HERT) | New Eqp |  | 51 | 2 |  |  |  | 8306-02 |  | MD3 | 1 |  | 236 |  | Utility Boiler | Babcock and Wilcox | Cyclone boiler |  |  |  | No. 6 oil | No. 2 oil |  |  | 0.27 |  | 48 hrs/year operation | [5 empty] | 2010-2009 average | 731.05 | 1233270 | 1233270 | 0.27 |  | 166.49 | CAIR-OS (max last 3 yrs) | 1084 | 1790536 | 0.21 |  | 189.3 |  | 8306-02-01 | 1 | Separated Overfired Air / High Energy Reagent Technology (SOFA/HERT) | New Eqp | 2 - Prog | [12 empty] | 2010-2009 average |  | 0.15 |  | 92.5 | 92.5 | 92.4952 |  |  | 73.99 | 0.44441 | 0.44444 | 0.44444 |  |  |  | 0.11747 |  | 105.1667 | 84.1333 | 0.44444 | 0.44062 | 0.44444 |  | Separated Overfired Air / High Energy Reagent Technology (SOFA/HERT) | Stk provided separate costs for each of the systems - SOFA (Eqp # 1) and HERT (Eqp # 2) | 4644456 | 1162830 | 822670 | 50000 | 30000 | 100000 | [8 empty] | 100000 |  | 1002670 | 60160 | 1143039 | 500000 | 60000 | 20000 | 13339 | 435000 |  |  | 50000 | [6 empty] | 1078339 | 64700 | 2305869 | 1 | 2305869 |  |  | 1037641.05 | 1037641.05 | 167175.5025 | 334351.005 | 167175.5025 |  |  |  |  | 668702.01 |  |  |  | 601831.809 | 25410.6764 | 5000 |  |  | 4614043.869 |  |  | 4614043.869 | 2305869 | 1322670 | 0.57361 | 708339 | 0.30719 | 0 | 0 | 2031009 | 0.8808 | 50000 | 0.021684 | 0 | 0 | 100000 | 0.043368 | 2081009 | 124860 | 0.06 | 0 | 9770.6314 | 1037641.05 | 0.45 | 668702.01 | 0.29 | 0.2 | 601831.809 | 0.261 | 0.15 | 4614043.869 | 4644454.5454 | -3.132e-07 | 19679.8921 | 1539374 | 20803 | 73.99 | -0.00010397 |  |  | 5000 | 340319 | 345319 |  |  | 1194055 | 1539374 | 5000 | 340319 | 345319 |  |  | 1194055 | 1539374 | 1539374 | 0 |  | 20803 | 18296.8384 | 2 | 2081009 | 100000 | 0 | 124860.54 | 2305869.54 | 9770.6336 | 1037641.293 | 668702.1666 |  | 601831.9499 | 601831.9499 | 25410.6823 | 0 |  |  | 4639455.6319 |  |  | 4639455.6319 | stk added + 0% | 19658.7103 |  |  | 5000 | 6.8395 | 340319 | 0.27595 | 345319 | 0 | 0 | 0 |  | 345319 | 345319 | 0.49807 |  |  | 345319 | 0.49807 | 2 | 348001.5718 | 693320.5718 | 1539374 | 0.54961 | stk added + 55% |  |  | 9370.4632 | 8240.7358 | 236 | Other | 4639455.6319 | 4639455.6319 |  |  |  | N/A |  | 4639455.6319 |  |  |  | 4639455.6319 | 2 | 1084 | 1790536 | 84.1333 | 22.1402 | 0.090158 | 17572.0482 |  |  |  | 46009.296 | 52398.24 | 35137.6433 | 41111.3881 | 496503.2192 | 49650.3219 | 720810.1085 | 113719.4048 | 18859.3871 | 132578.7919 | 459433.6242 | 592012.4162 | 1312822.5247 | 537160.8 | 21869.9247 | 559030.7247 | 79547.2752 | 185578.2253 | 2 | 348001.5718 | 613127.0722 | 1925949.5969 |  | 26029.8635 | 22891.6355
|  |  | 8306-02-02 | Selective Catalytic Reduction (SCR) with ID fans | SCR |  | 1: 52; 33: #N/A; 45: 8306-02-02; 46: 2; 47: Selective Catalytic Reduction (SCR) with ID fans; 48: SCR; 49: 4 - Custom; 62: 2010-2009 average; 64: 0.1; 66: 61.66; 67: 61.66; 68: 61.6635; 71: 104.83; 72: 0.62965; 73: 0.62963; 74: 0.9; 78: 0.021145; 80: 18.93; 81: 170.37; 82: 0.9; 83: 0.89931; 84: 0.9; 85: 0.9; 86: Selective Catalytic Reduction (SCR) with ID fans; 88: 101740654; 89: 27499579; 90: 21009841; 91: 1573093; 92: 698849; 93: 1715272; 95: 1105017; 97: 1397507; 104: 27499579; 123: 27499579; 124: 1; 125: 27499579; 126: 432189; 127: 46419590; 129: 46851779; 134: 633491; 135: 20072729; 136: 6683075.5; 137: 27389295.5; 146: 101740653.5; 149: 101740653.5; 150: 27499579; 151: 21009841; 152: 0.76401; 153: 5092231; 154: 0.18517; 155: 0; 156: 0; 157: 26102072; 158: 0.94918; 159: 1397507; 160: 0.050819; 161: 0; 162: 0; 163: 0; 164: 0; 165: 27499579; 168: 0; 169: 116523.6398; 170: 46851779; 171: 1.7037; 172: 27389295.5; 173: 0.99599; 174: 0.36838; 178: 101740653.5; 179: 101740653.5; 180: -4.9145e-09; 181: 431104.464; 182: 26361800; 183: 251477; 184: 104.83; 185: 2.0253e-05; 188: 20000; 189: 185045; 190: 205045; 193: 26156755; 194: 26361800; 195: 20000; 196: 185045; 197: 205045; 200: 26156755; 201: 26361800; 202: 26361800; 203: 0; 205: 251477; 206: 154732.6407; 207: 4; 208: 27499579; 209: 0; 210: 0; 212: 27499579; 213: 116523.6398; 214: 46851779; 215: 27389295.5; 218: 0; 223: 101740653.5; 226: 101740653.5; 227: same TCC; 228: 431104.464; 231: 20000; 232: 27.3579; 233: 185045; 234: 0.15004; 235: 205045; 236: 0; 237: 0; 238: 0; 240: 205045; 241: 205045; 242: 0.026165; 245: 205045; 246: 0.026165; 247: 2; 248: 7631478.8075; 249: 7836523.8075; 250: 26361800; 251: 0.70273; 252: stk added + 70%; 255: 74754.5913; 256: 45997.0876; 257: 236; 258: SCR; 259: 101740653.5; 260: 101740653.5; 264: 12188200; 265: 21085586; 266: 101740653.5; 270: 101740653.5; 271: 2; 272: 1084; 273: 1790536; 274: 170.37; 275: 22.1402; 276: 0.090158; 277: 17572.0482; 281: 46009.296; 282: 106106.436; 283: 71153.7277; 284: 41111.3881; 285: 496503.2192; 286: 49650.3219; 287: 810534.3889; 288: 113719.4048; 289: 85712.9071; 290: 199432.3119; 291: 459433.6242; 292: 658865.9361; 293: 1469400.325; 294: 537160.8; 295: 21869.9247; 296: 559030.7247; 297: 119659.3871; 298: 843423.44; 299: 2; 300: 7631478.8075; 301: 8594561.6346; 302: 10063961.9596; 304: 96002.6897; 305: 59071.2095
[7 empty] | 53 | [234 empty] | 0
8306-03 | NRG | MD4 | 8306-03-01 | Separated Overfired Air / High Energy Reagent Technology (SOFA/HERT) | New Eqp |  | 54 | 3 |  |  |  | 8306-03 |  | MD4 | 1 |  | 400 |  | Utility Boiler | Combustion Engineering | Tangential fired |  |  |  | No. 6 oil | No. 2 oil |  |  | 0.28 |  | 48 hrs/year operation | [5 empty] | 2010-2009 average | 243.6 | 557770 | 557770 | 0.28 |  | 78.09 | CAIR-OS (max last 3 yrs) | 461 | 880454 | 0.18 |  | 80.5 |  | 8306-03-01 | 1 | Separated Overfired Air / High Energy Reagent Technology (SOFA/HERT) | New Eqp | 2 - Prog | [12 empty] | 2010-2009 average |  | 0.15 |  | 41.83 | 41.83 | 41.8327 |  |  | 36.26 | 0.46434 | 0.46429 | 0.46429 |  |  |  | 0.097961 |  | 43.125 | 37.375 | 0.46429 | 0.45577 | 0.46429 |  | Separated Overfired Air / High Energy Reagent Technology (SOFA/HERT) |  | 6213828 | 1480950 | 1041250 | 250000 | 30000 | 50000 | [8 empty] | 0 |  | 1371250 | 109700 | 1597960 | 500000 | 217000 | 20000 |  | 600000 |  |  | 50000 |  |  |  |  | 100000 |  | 1387000 | 110960 | 3078910 | 1 | 3078910 |  |  | 1385509.5 | 1385509.5 | 223220.975 | 446441.95 | 223220.975 |  |  |  |  | 892883.9 |  |  |  | 803595.51 | 33929.5882 | 19000 |  |  | 6160898.91 |  |  | 6160898.91 | 3078910 | 1541250 | 0.50058 | 1167000 | 0.37903 | 0 | 0 | 2708250 | 0.87961 | 50000 | 0.01624 | 0 | 0 | 100000 | 0.032479 | 2758250 | 220660 | 0.08 | 0 | 7697.275 | 1385509.5 | 0.45 | 892883.9 | 0.29 | 0.2 | 803595.51 | 0.261 | 0.15 | 6160898.91 | 6213828.4982 | 8.0176e-08 | 15534.5712 | 1780244 | 49103 | 36.26 | 0.00012962 |  |  | 20000 | 162716 | 182716 |  |  | 1597528 | 1780244 | 20000 | 162716 | 182716 |  |  | 1597528 | 1780244 | 1780244 | 0 |  | 49103 | 47631.9465 | 2 | 2758250 | 100000 | 0 | 165495 | 3023745 | 7559.3625 | 1360685.25 | 876886.05 |  | 789197.445 | 789197.445 | 33321.6699 | 0 |  |  | 6083835.4149 |  |  | 6083835.4149 | stk added + 2% | 15209.5885 |  |  | 20000 | 82.1018 | 162716 | 0.29173 | 182716 | 0 | 0 | 0 |  | 182716 | 182716 | 0.28591 |  |  | 182716 | 0.28591 | 2 | 456343.2555 | 639059.2555 | 1780244 | 0.64103 | stk added + 64% |  |  | 17624.3589 | 17098.5754 | 400 | Other | 6083835.4149 | 6083835.4149 |  |  |  | N/A |  | 6083835.4149 |  |  |  | 6083835.4149 | 2 | 461 | 880454 | 37.375 | 52.0607 | 0.07213 | 29783.1325 |  |  |  | 19566.684 | 23277.15 | 15609.3829 | 55747.2594 | 357883.52 | 35788.352 | 507872.3484 | 48362.2192 | 10517.4305 | 58879.6497 |  | 58879.6497 | 566751.998 | 264136.2 | 20617.0076 | 284753.2076 | 35327.7898 | 243353.4166 | 2 | 456343.2555 | 735024.4619 | 1301776.46 |  | 35901.171 | 34830.1394
|  |  | 8306-03-02 | Selective Catalytic Reduction (SCR) with ID fans | SCR |  | 1: 55; 33: #N/A; 45: 8306-03-02; 46: 2; 47: Selective Catalytic Reduction (SCR) with ID fans; 48: SCR; 49: 4 - Custom; 62: 2010-2009 average; 64: 0.1; 66: 27.89; 67: 27.89; 68: 27.8885; 71: 50.2; 72: 0.64285; 73: 0.64286; 74: 0.9; 78: 0.018286; 80: 8.05; 81: 72.45; 82: 0.9; 83: 0.89841; 84: 0.9; 85: 0.9; 86: Selective Catalytic Reduction (SCR) with ID fans; 88: 145353267; 89: 48186953; 90: 28013121; 91: 12971822; 92: 2308584; 93: 1715272; 95: 1431270; 97: 1746884; 104: 48186953; 123: 48186953; 124: 1; 125: 48186953; 126: 636052; 127: 61600978; 129: 62237030; 134: 708504; 135: 25701681; 136: 8519100; 137: 34929285; 146: 145353268; 149: 145353268; 150: 48186953; 151: 28013121; 152: 0.58134; 153: 18426948; 154: 0.38241; 155: 0; 156: 0; 157: 46440069; 158: 0.96375; 159: 1746884; 160: 0.036252; 161: 0; 162: 0; 163: 0; 164: 0; 165: 48186953; 168: 0; 169: 120467.3825; 170: 62237030; 171: 1.2916; 172: 34929285; 173: 0.72487; 174: 0.31632; 178: 145353268; 179: 145353268; 180: 6.8798e-09; 181: 363383.17; 182: 37497929; 183: 746981; 184: 50.2; 185: 1.3793e-05; 188: 20000; 189: 108700; 190: 128700; 193: 37369229; 194: 37497929; 195: 20000; 196: 108700; 197: 128700; 200: 37369229; 201: 37497929; 202: 37497929; 203: 0; 205: 746981; 206: 517569.7585; 207: 4; 208: 48186953; 209: 0; 210: 0; 212: 48186953; 213: 120467.3825; 214: 62237030; 215: 34929285; 218: 0; 223: 145353268; 226: 145353268; 227: same TCC; 228: 363383.17; 231: 20000; 232: 82.1018; 233: 108700; 234: 0.19488; 235: 128700; 236: 0; 237: 0; 238: 0; 240: 128700; 241: 128700; 242: 0.011667; 245: 128700; 246: 0.011667; 247: 2; 248: 10902823.4651; 249: 11031523.4651; 250: 37497929; 251: 0.70581; 252: stk added + 71%; 255: 219751.4634; 256: 152263.954; 257: 400; 258: Combined; 259: 145353268; 260: 145353268; 264: N/A; 266: 145353268; 270: 145353268; 271: 2; 272: 461; 273: 880454; 274: 72.45; 275: 52.0607; 276: 0.07213; 277: 29783.1325; 281: 19566.684; 282: 45121.86; 283: 30258.1885; 284: 55747.2594; 285: 357883.52; 286: 35788.352; 287: 544365.8639; 288: 48362.2192; 289: 251279.4621; 290: 299641.6813; 292: 299641.6813; 293: 844007.5452; 294: 264136.2; 295: 20617.0076; 296: 284753.2076; 297: 179785.0088; 298: 5814130.72; 299: 2; 300: 10902823.4651; 301: 16896739.1939; 302: 17740746.7391; 304: 353401.3295; 305: 244868.8301
|  |  | 8306-03-03 | Selective Catalytic Reduction (SCR) | SCR |  | 1: 56; 33: #N/A; 45: 8306-03-03; 46: 3; 47: Selective Catalytic Reduction (SCR); 48: SCR; 49: 4 - Custom; 62: 2010-2009 average; 64: 0.1; 66: 27.89; 67: 27.89; 68: 27.8885; 71: 50.2; 72: 0.64285; 73: 0.64286; 74: 0.9; 78: 0.018286; 80: 8.05; 81: 72.45; 82: 0.9; 83: 0.89841; 84: 0.9; 85: 0.9; 86: Selective Catalytic Reduction (SCR); 88: 106812093; 89: 32426295; 90: 28013121; 91: 50000; 92: 203697; 93: 1715272; 95: 697321; 97: 1746884; 104: 32426295; 123: 32426295; 124: 1; 125: 32426295; 126: 636052; 127: 46530759; 129: 47166811; 134: 633491; 135: 19674495; 136: 6911001; 137: 27218987; 146: 106812093; 149: 106812093; 150: 32426295; 151: 28013121; 152: 0.8639; 153: 2666290; 154: 0.082226; 155: 0; 156: 0; 157: 30679411; 158: 0.94613; 159: 1746884; 160: 0.053872; 161: 0; 162: 0; 163: 0; 164: 0; 165: 32426295; 168: 0; 169: 81065.7375; 170: 47166811; 171: 1.4546; 172: 27218987; 173: 0.83941; 178: 106812093; 179: 106812093; 180: 0; 181: 267030.2325; 182: 27528526; 183: 548385; 184: 50.2; 185: 1.4566e-05; 188: 20000; 189: 47943; 190: 67943; 193: 27460583; 194: 27528526; 195: 20000; 196: 47943; 197: 67943; 200: 27460583; 201: 27528526; 202: 27528526; 203: 0; 205: 548385; 206: 379965.8523; 207: 4; 208: 32426295; 209: 0; 210: 0; 212: 32426295; 213: 81065.7375; 214: 47166811; 215: 27218987; 218: 0; 223: 106812093; 226: 106812093; 227: same TCC; 228: 267030.2325; 231: 20000; 232: 82.1018; 233: 47943; 234: 0.085955; 235: 67943; 236: 0; 237: 0; 238: 0; 240: 67943; 241: 67943; 242: 0.008409; 245: 67943; 246: 0.008409; 247: 2; 248: 8011883.1172; 249: 8079826.1172; 250: 27528526; 251: 0.70649; 252: stk added + 71%; 255: 160952.7115; 256: 111522.7897; 257: 400; 258: SCR; 259: 106812093; 260: 106812093; 264: 20339000; 265: 35186470; 266: 106812093; 270: 106812093; 271: 2; 272: 461; 273: 880454; 274: 72.45; 275: 52.0607; 276: 0.07213; 277: 29783.1325; 281: 19566.684; 282: 45121.86; 283: 30258.1885; 284: 55747.2594; 285: 357883.52; 286: 35788.352; 287: 544365.8639; 288: 48362.2192; 289: 60828.61; 290: 109190.8292; 292: 109190.8292; 293: 653556.6931; 294: 264136.2; 295: 20617.0076; 296: 284753.2076; 297: 65514.4975; 298: 1407458.8; 299: 2; 300: 8011883.1172; 301: 9484856.4147; 302: 10138413.1079; 304: 201960.4205; 305: 139936.6889
[7 empty] | 57 | [234 empty] | 0
8306-04 | NRG | MV5 | 8306-04-01 | Close Coupled Over Fire Air (CCOFA) | New Eqp |  | 58 | 4 |  |  |  | 8306-04 | Montville | MV5 | 1 |  | 81 | 488.5 | Utility Boiler | Combustion Engineering | Tangential fired |  |  |  | No. 6 oil | Nat. Gas |  |  | 0.23 |  | 48 hrs/year operation | [5 empty] | 2010-2009 average | 573.9 | 352730 | 352730 | 0.23 |  | 40.56 | CAIR-OS (max last 3 yrs) | 932 | 567960 | 0.1 |  | 27.4 |  | 8306-04-01 | 1 | Close Coupled Over Fire Air (CCOFA) | New Eqp | 2 - Prog | [12 empty] | 2010-2009 average |  | 0.15 |  | 26.45 | 26.45 | 26.4548 |  |  | 14.11 | 0.34788 | 0.34783 | 0.34783 |  |  |  | 0.062925 |  | 17.8696 | 9.5304 | 0.34783 | 0.37075 | 0.34783 |  | Close Coupled Over Fire Air (CCOFA) |  | 1950050 | 969200 | 600000 | 150000 | 20000 | 50000 | [8 empty] | 100000 |  | 820000 | 49200 | [17 empty] | 969200 | 1 | 969200 |  |  | 436140 | 436140 | 70267 | 140534 | 70267 |  |  |  |  | 281068 |  |  |  | 252961.2 | 10680.584 | 0 |  |  | 1939369.2 |  |  | 1939369.2 | 969200 | 600000 | 0.61907 | 220000 | 0.22699 | 0 | 0 | 820000 | 0.84606 | 0 | 0 | 0 | 0 | 100000 | 0.10318 | 820000 | 49200 | 0.06 | 0 | 11965.4321 | 436140 | 0.45 | 281068 | 0.29 | 0.2 | 252961.2 | 0.261 | 0.15 | 1939369.2 | 1950049.784 | -1.1077e-07 | 24074.6887 | 525860 | 37271 | 14.11 | 6.4291e-05 |  |  | 20000 | 4517 | 24517 |  |  | 501343 | 525860 | 20000 | 4517 | 24517 |  |  | 501343 | 525860 | 525860 | 0 |  | 37271 | 55176.9161 | 2 | 820000 | 100000 | 0 | 49200 | 969200 | 11965.4321 | 436140 | 281068 |  | 252961.2 | 252961.2 | 10680.584 | 0 |  |  | 1950049.784 |  |  | 1950049.784 | same TCC | 24074.6887 |  |  | 20000 | 34.8493 | 4517 | 0.012806 | 24517 | 0 | 0 | 0 |  | 24517 | 24517 | 0.14355 |  |  | 24517 | 0.14355 | 2 | 146271.5551 | 170788.5551 | 525860 | 0.67522 | stk added + 68% |  |  | 12104.079 | 17920.332 | 81 | Other | 1950049.784 | 1950049.784 |  |  |  | N/A |  | 1950049.784 |  |  |  | 1950049.784 | 2 | 932 | 567960 | 9.5304 | 25.7511 | 0.084861 | 6031.0843 |  |  |  | 39557.808 | 5935.5548 | 3980.3132 | 13281.2859 | 146514.8736 | 14651.4874 | 223921.3228 | 97773.5104 | 6815.424 | 104588.9344 | 148422.848 | 253011.7824 | 476933.1053 | 170388 | 21643.1249 | 192031.1249 | 62753.3606 | 78001.9914 | 2 | 146271.5551 | 287026.9071 | 763960.0123 |  | 54143.1618 | 80160.0378
|  |  | 8306-04-02 | (HERT) High Energy Reagent Technology SNCR | New Eqp |  | 1: 59; 33: #N/A; 45: 8306-04-02; 46: 2; 47: (HERT) High Energy Reagent Technology SNCR; 48: New Eqp; 49: 2 - Prog; 62: 2010-2009 average; 64: 0.15; 66: 26.45; 67: 26.45; 68: 26.4548; 71: 14.11; 72: 0.34788; 73: 0.34783; 74: 0.34783; 78: 0.062925; 80: 17.8696; 81: 9.5304; 82: 0.34783; 83: 0.37075; 84: 0.34783; 86: (HERT) High Energy Reagent Technology SNCR; 88: 1602413; 89: 796420; 90: 250000; 91: 237000; 92: 20000; 94: 100000; 97: 50000; 102: 100000; 104: 657000; 105: 39420; 123: 796420; 124: 1; 125: 796420; 128: 358389; 129: 358389; 130: 57740.45; 131: 115480.9; 132: 57740.45; 137: 230961.8; 141: 207865.62; 142: 8776.5484; 143: 0; 146: 1593636.42; 149: 1593636.42; 150: 796420; 151: 250000; 152: 0.3139; 153: 357000; 154: 0.44826; 155: 0; 156: 0; 157: 607000; 158: 0.76216; 159: 50000; 160: 0.062781; 161: 0; 162: 0; 163: 100000; 164: 0.12556; 165: 657000; 166: 39420; 167: 0.06; 168: 0; 169: 9832.3457; 170: 358389; 171: 0.45; 172: 230961.8; 173: 0.29; 174: 0.2; 175: 207865.62; 176: 0.261; 177: 0.15; 178: 1593636.42; 179: 1602412.9684; 180: -1.972e-08; 181: 19782.8762; 182: 569623; 183: 40372; 184: 14.11; 185: 4.5502e-05; 188: 20000; 189: 137655; 190: 157655; 193: 411968; 194: 569623; 195: 20000; 196: 137655; 197: 157655; 200: 411968; 201: 569623; 202: 569623; 203: 0; 205: 40372; 206: 59768.8367; 207: 2; 208: 657000; 209: 100000; 210: 0; 211: 39420; 212: 796420; 213: 9832.3457; 214: 358389; 215: 230961.8; 217: 207865.62; 218: 207865.62; 219: 8776.5484; 220: 0; 223: 1602412.9684; 226: 1602412.9684; 227: same TCC; 228: 19782.8762; 231: 20000; 232: 34.8493; 233: 137655; 234: 0.39026; 235: 157655; 236: 0; 237: 0; 238: 0; 240: 157655; 241: 157655; 242: 0.56741; 245: 157655; 246: 0.56741; 247: 2; 248: 120195.6169; 249: 277850.6169; 250: 569623; 251: 0.51222; 252: stk added + 51%; 255: 19691.7517; 256: 29154.0337; 257: 81; 258: Other; 259: 1602412.9684; 260: 1602412.9684; 264: N/A; 266: 1602412.9684; 270: 1602412.9684; 271: 2; 272: 932; 273: 567960; 274: 9.5304; 275: 25.7511; 276: 0.084861; 277: 6031.0843; 281: 39557.808; 282: 5935.5548; 283: 3980.3132; 284: 13281.2859; 285: 146514.8736; 286: 14651.4874; 287: 223921.3228; 288: 97773.5104; 289: 5600.4333; 290: 103373.9437; 291: 148422.848; 292: 251796.7918; 293: 475718.1146; 294: 170388; 295: 21643.1249; 296: 192031.1249; 297: 62024.3662; 298: 64096.5187; 299: 2; 300: 120195.6169; 301: 246316.5019; 302: 722034.6164; 304: 51171.8367; 305: 75760.9315
|  |  | 8306-04-03 | Selective Catalytic Reduction (SCR) | SCR |  | 1: 60; 33: #N/A; 45: 8306-04-03; 46: 3; 47: Selective Catalytic Reduction (SCR); 48: SCR; 49: 4 - Custom; 62: 2010-2009 average; 64: 0.15; 66: 26.45; 67: 26.45; 68: 26.4548; 71: 14.11; 72: 0.34788; 73: 0.34783; 74: 0.9; 76: 4.8243e-05; 78: 0.0096486; 80: 2.74; 81: 24.66; 82: 0.9; 83: 0.90351; 84: 0.9; 85: 0.9; 86: Selective Catalytic Reduction (SCR); 88: 65452696; 89: 15739444; 90: 11205248; 91: 1047064; 92: 733549; 93: 1184506; 95: 695635; 97: 873442; 104: 15739444; 123: 15739444; 124: 1; 125: 15739444; 126: 371030; 127: 30607972; 129: 30979002; 134: 558479; 135: 13328721; 136: 4847050; 137: 18734250; 146: 65452696; 149: 65452696; 150: 15739444; 151: 11205248; 152: 0.71192; 153: 3660754; 154: 0.23258; 155: 0; 156: 0; 157: 14866002; 158: 0.94451; 159: 873442; 160: 0.055494; 161: 0; 162: 0; 163: 0; 164: 0; 165: 15739444; 168: 0; 169: 194314.1235; 170: 30979002; 171: 1.9682; 172: 18734250; 173: 1.1903; 178: 65452696; 179: 65452696; 180: 0; 181: 808057.9753; 182: 16888516; 183: 1196986; 184: 14.11; 185: 5.6631e-05; 188: 4700; 189: 56422; 190: 61122; 193: 16827394; 194: 16888516; 195: 4700; 196: 56422; 197: 61122; 200: 16827394; 201: 16888516; 202: 16888516; 203: 0; 205: 1196986; 206: 684854.6634; 207: 4; 208: 15739444; 209: 0; 210: 0; 212: 15739444; 213: 194314.1235; 214: 30979002; 215: 18734250; 218: 0; 223: 65452696; 226: 65452696; 227: same TCC; 228: 808057.9753; 231: 4700; 232: 8.1896; 233: 56422; 234: 0.15996; 235: 61122; 236: 0; 237: 0; 238: 0; 240: 61122; 241: 61122; 242: 0.012297; 245: 61122; 246: 0.012297; 247: 2; 248: 4909550.3639; 249: 4970672.3639; 250: 16888516; 251: 0.70568; 252: stk added + 71%; 255: 352280.1108; 256: 201568.2224; 257: 81; 258: SCR; 259: 65452696; 260: 65452696; 264: 4484700; 265: 7758531; 266: 7758531; 270: 7758531; 271: 2; 272: 932; 273: 567960; 274: 24.66; 275: 25.7511; 276: 0.084861; 277: 6031.0843; 281: 39557.808; 282: 15358.248; 283: 10299.0604; 284: 13281.2859; 285: 146514.8736; 286: 14651.4874; 287: 239662.7633; 288: 97773.5104; 289: 27116.0658; 290: 124889.5762; 291: 148422.848; 292: 273312.4243; 293: 512975.1875; 294: 170388; 295: 21643.1249; 296: 192031.1249; 297: 74933.7457; 298: 310341.24; 299: 2; 300: 581960.7292; 301: 967235.715; 302: 1480210.9025; 304: 104905.0959; 305: 60024.773
[7 empty] | 61 | [36 empty] | CAIR-OS (max last 3 yrs) | [197 empty] | 0
8306-05 | NRG | MV6 | 8306-05-01 | Separated Overfired Air / High Energy Reagent Technology (SOFA/HERT) | New Eqp |  | 62 | 5 |  |  |  | 8306-05 |  | MV6 | 1 |  | 402 |  | Utility Boiler | Combustion Engineering | Tangential fired |  |  |  | No. 6 oil | No. 2 oil |  |  | 0.27 |  | 48 hrs/year operation | [5 empty] | 2010-2009 average | 231.15 | 448035 | 448035 | 0.27 |  | 60.48 | CAIR-OS (max last 3 yrs) | 376 | 608716 | 0.15 |  | 44.3 |  | 8306-05-01 | 1 | Separated Overfired Air / High Energy Reagent Technology (SOFA/HERT) | New Eqp | 2 - Prog | [12 empty] | 2010-2009 average |  | 0.15 |  | 33.6 | 33.6 | 33.6026 |  |  | 26.88 | 0.44444 | 0.44444 | 0.44444 |  |  |  | 0.080862 |  | 24.6111 | 19.6889 | 0.44444 | 0.46092 | 0.44444 |  | Separated Overfired Air / High Energy Reagent Technology (SOFA/HERT) |  | 6077989 | 1509376 | 999500 | 250100 | 30000 | 50000 | [8 empty] | 100000 |  | 1329600 | 79776 | 1502020 | 500000 | 267000 |  |  | 600000 |  |  | 50000 | [6 empty] | 1417000 | 85020 | 3011396 | 1 | 3011396 |  |  | 1355128.2 | 1355128.2 | 218326.21 | 436652.42 | 218326.21 |  |  |  |  | 873304.84 |  |  |  | 785974.356 | 33185.5839 | 19000 |  |  | 6025803.396 |  |  | 6025803.396 | 3011396 | 1499500 | 0.49794 | 1197100 | 0.39752 | 0 | 0 | 2696600 | 0.89547 | 50000 | 0.016604 | 0 | 0 | 100000 | 0.033207 | 2746600 | 164796 | 0.06 | 0 | 7491.0348 | 1355128.2 | 0.45 | 873304.84 | 0.29 | 0.2 | 785974.356 | 0.261 | 0.15 | 6025803.396 | 6077988.9799 | -3.3037e-09 | 15119.3756 | 1746297 | 64961 | 26.88 | -8.3223e-05 |  |  | 20000 | 163692 | 183692 |  |  | 1562605 | 1746297 | 20000 | 163692 | 183692 |  |  | 1562605 | 1746297 | 1746297 | 0 |  | 64961 | 88694.5429 | 2 | 2746600 | 100000 | 0 | 164796 | 3011396 | 7491.0348 | 1355128.2 | 873304.84 |  | 785974.356 | 785974.356 | 33185.5839 | 0 |  |  | 6058988.9799 |  |  | 6058988.9799 | stk added + 0% | 15072.1119 |  |  | 20000 | 86.5239 | 163692 | 0.36536 | 183692 | 0 | 0 | 0 |  | 183692 | 183692 | 0.28784 |  |  | 183692 | 0.28784 | 2 | 454479.5458 | 638171.5458 | 1746297 | 0.63456 | stk added + 63% |  |  | 23741.501 | 32412.776 | 402 | Other | 6058988.9799 | 6058988.9799 |  |  |  | N/A |  | 6058988.9799 |  |  |  | 6058988.9799 | 2 | 376 | 608716 | 19.6889 | 63.8298 | 0.070945 | 29932.0482 |  |  |  | 15958.944 | 12262.24 | 8222.9139 | 55105.4613 | 293355.8016 | 29335.5802 | 414240.9409 | 39445.1072 | 8543.1745 | 47988.2817 |  | 47988.2817 | 462229.2226 | 182614.8 | 20329.1036 | 202943.9036 | 28792.969 | 242359.5592 | 2 | 454479.5458 | 725632.074 | 1187861.2966 |  | 44191.2685 | 60331.5557
|  |  | 8306-05-02 | Selective Catalytic Reduction (SCR) with ID fans | SCR |  | 1: 63; 33: #N/A; 45: 8306-05-02; 46: 2; 47: Selective Catalytic Reduction (SCR) with ID fans; 48: SCR; 49: 4 - Custom; 62: 2010-2009 average; 64: 0.1; 66: 22.4; 67: 22.4; 68: 22.4017; 71: 38.08; 72: 0.62963; 73: 0.62963; 74: 0.9; 78: 0.014555; 80: 4.43; 81: 39.87; 82: 0.9; 83: 0.90297; 84: 0.9; 85: 0.9; 86: Selective Catalytic Reduction (SCR) with ID fans; 88: 145353267; 89: 48186953; 90: 28013121; 91: 12971822; 92: 2308584; 93: 1715272; 95: 1431270; 97: 1746884; 104: 48186953; 123: 48186953; 124: 1; 125: 48186953; 126: 636052; 127: 61600978; 129: 62237030; 134: 708504; 135: 25701681; 136: 8519100; 137: 34929285; 146: 145353268; 149: 145353268; 150: 48186953; 151: 28013121; 152: 0.58134; 153: 18426948; 154: 0.38241; 155: 0; 156: 0; 157: 46440069; 158: 0.96375; 159: 1746884; 160: 0.036252; 161: 0; 162: 0; 163: 0; 164: 0; 165: 48186953; 168: 0; 169: 119868.0423; 170: 62237030; 171: 1.2916; 172: 34929285; 173: 0.72487; 174: 0.31632; 178: 145353268; 179: 145353268; 180: 6.8798e-09; 181: 361575.2935; 182: 37494555; 183: 984549; 184: 38.08; 185: -7.8126e-05; 188: 20000; 189: 105326; 190: 125326; 193: 37369229; 194: 37494555; 195: 20000; 196: 105326; 197: 125326; 200: 37369229; 201: 37494555; 202: 37494555; 203: 0; 205: 984549; 206: 940420.2408; 207: 4; 208: 48186953; 209: 0; 210: 0; 212: 48186953; 213: 119868.0423; 214: 62237030; 215: 34929285; 218: 0; 223: 145353268; 226: 145353268; 227: same TCC; 228: 361575.2935; 231: 20000; 232: 86.5239; 233: 105326; 234: 0.23508; 235: 125326; 236: 0; 237: 0; 238: 0; 240: 125326; 241: 125326; 242: 0.011364; 245: 125326; 246: 0.011364; 247: 2; 248: 10902823.4651; 249: 11028149.4651; 250: 37494555; 251: 0.70587; 252: stk added + 71%; 255: 289604.7654; 256: 276602.6954; 257: 402; 258: Combined; 259: 145353268; 260: 145353268; 264: N/A; 266: 145353268; 270: 145353268; 271: 2; 272: 376; 273: 608716; 274: 39.87; 275: 63.8298; 276: 0.070945; 277: 29932.0482; 281: 15958.944; 282: 24831.036; 283: 16651.4006; 284: 55105.4613; 285: 293355.8016; 286: 29335.5802; 287: 435238.2236; 288: 39445.1072; 289: 204948.1079; 290: 244393.2151; 292: 244393.2151; 293: 679631.4387; 294: 182614.8; 295: 20329.1036; 296: 202943.9036; 297: 146635.929; 298: 5814130.72; 299: 2; 300: 10902823.4651; 301: 16863590.1142; 302: 17543221.5529; 304: 460693.8433; 305: 440010.5732
|  |  | 8306-05-03 | Selective Catalytic Reduction (SCR) | SCR |  | 1: 64; 33: #N/A; 45: 8306-05-03; 46: 3; 47: Selective Catalytic Reduction (SCR); 48: SCR; 49: 4 - Custom; 62: 2010-2009 average; 64: 0.1; 66: 22.4; 67: 22.4; 68: 22.4017; 71: 38.08; 72: 0.62963; 73: 0.62963; 74: 0.9; 78: 0.014555; 80: 4.43; 81: 39.87; 82: 0.9; 83: 0.90297; 84: 0.9; 85: 0.9; 86: Selective Catalytic Reduction (SCR); 88: 106812093; 89: 32426295; 90: 28013121; 91: 50000; 92: 203697; 93: 1715272; 95: 697321; 97: 1746884; 104: 32426295; 123: 32426295; 124: 1; 125: 32426295; 126: 636052; 127: 46530759; 129: 47166811; 134: 633491; 135: 19674495; 136: 6911001; 137: 27218987; 146: 106812093; 149: 106812093; 150: 32426295; 151: 28013121; 152: 0.8639; 153: 2666290; 154: 0.082226; 155: 0; 156: 0; 157: 30679411; 158: 0.94613; 159: 1746884; 160: 0.053872; 161: 0; 162: 0; 163: 0; 164: 0; 165: 32426295; 168: 0; 169: 80662.4254; 170: 47166811; 171: 1.4546; 172: 27218987; 173: 0.83941; 178: 106812093; 179: 106812093; 180: 0; 181: 265701.7239; 182: 27526781; 183: 722811; 184: 38.08; 185: -7.768e-05; 188: 20000; 189: 46198; 190: 66198; 193: 27460583; 194: 27526781; 195: 20000; 196: 46198; 197: 66198; 200: 27460583; 201: 27526781; 202: 27526781; 203: 0; 205: 722811; 206: 690413.3684; 207: 4; 208: 32426295; 209: 0; 210: 0; 212: 32426295; 213: 80662.4254; 214: 47166811; 215: 27218987; 218: 0; 223: 106812093; 226: 106812093; 227: same TCC; 228: 265701.7239; 231: 20000; 232: 86.5239; 233: 46198; 234: 0.10311; 235: 66198; 236: 0; 237: 0; 238: 0; 240: 66198; 241: 66198; 242: 0.0081948; 245: 66198; 246: 0.0081948; 247: 2; 248: 8011883.1172; 249: 8078081.1172; 250: 27526781; 251: 0.70654; 252: stk added + 71%; 255: 212134.4831; 256: 202610.5121; 257: 402; 258: SCR; 259: 106812093; 260: 106812093; 264: 20438400; 265: 35358432; 266: 106812093; 270: 106812093; 271: 2; 272: 376; 273: 608716; 274: 39.87; 275: 63.8298; 276: 0.070945; 277: 29932.0482; 281: 15958.944; 282: 24831.036; 283: 16651.4006; 284: 55105.4613; 285: 293355.8016; 286: 29335.5802; 287: 435238.2236; 288: 39445.1072; 289: 49855.3891; 290: 89300.4963; 292: 89300.4963; 293: 524538.72; 294: 182614.8; 295: 20329.1036; 296: 202943.9036; 297: 53580.2978; 298: 1414337.28; 299: 2; 300: 8011883.1172; 301: 9479800.695; 302: 10004339.415; 304: 262718.9972; 305: 250923.9883
[7 empty] | 65 | [36 empty] | CAIR-OS (max last 3 yrs) | [197 empty] | 0
8306-06 | NRG | NH1 | 8306-06-01 | Separated Overfired Air / High Energy Reagent Technology (SOFA/HERT) | New Eqp |  | 66 | 6 |  |  |  | 8306-06 | Norwalk Harbor Station | NH1 | 1 |  | 164 | 353 | Utility Boiler | Combustion Engineering | Tangential fired |  |  |  | No. 6 oil | No. 2 oil |  |  | 0.21 |  | 48 hrs/year operation | [5 empty] | 2010-2009 average | 418.45 | 299765 | 299765 | 0.21 |  | 31.48 | CAIR-OS (max last 3 yrs) | 829 | 624903 | 0.16 |  | 49.5 |  | 8306-06-01 | 1 | Separated Overfired Air / High Energy Reagent Technology (SOFA/HERT) | New Eqp | 2 - Prog | [12 empty] | 2010-2009 average |  | 0.15 |  | 22.48 | 22.48 | 22.4824 |  |  | 9 | 0.2859 | 0.28571 | 0.28571 |  |  |  | 0.11316 |  | 35.3571 | 14.1429 | 0.28571 | 0.29275 | 0.28571 |  | Separated Overfired Air / High Energy Reagent Technology (SOFA/HERT) |  | 5857063 | 1860912 | 1481238 | 50000 | 30000 | 100000 | [8 empty] | 100000 |  | 1661238 | 99674 | 1047639 | 500000 | 35000 | 20000 | 13339 | 370000 |  |  | 50000 | [6 empty] | 988339 | 59300 | 2908551 | 1 | 2908551 |  |  | 1308847.95 | 1308847.95 | 210869.9475 | 421739.895 | 210869.9475 |  |  |  |  | 843479.79 |  |  |  | 759131.811 | 32052.232 | 5000 |  |  | 5820010.551 |  |  | 5820010.551 | 2908551 | 1981238 | 0.68118 | 618339 | 0.21259 | 0 | 0 | 2599577 | 0.89377 | 50000 | 0.017191 | 0 | 0 | 100000 | 0.034381 | 2649577 | 158974 | 0.06 | 0 | 17735.0671 | 1308847.95 | 0.45 | 843479.79 | 0.29 | 0.2 | 759131.811 | 0.261 | 0.15 | 5820010.551 | 5857062.783 | -3.7046e-08 | 35713.7975 | 1516150 | 168593 | 9 | 0.00078229 |  |  | 5000 | 5343 | 10343 |  |  | 1505807 | 1516150 | 5000 | 5343 | 10343 |  |  | 1505807 | 1516150 | 1516150 | 0 |  | 168593 | 107202.5253 | 2 | 2649577 | 100000 | 0 | 158974.62 | 2908551.62 | 17735.0709 | 1308848.229 | 843479.9698 |  | 759131.9728 | 759131.9728 | 32052.2389 | 0 |  |  | 5852064.0305 |  |  | 5852064.0305 | stk added + 0% | 35683.3173 |  |  | 5000 | 11.9489 | 5343 | 0.017824 | 10343 | 0 | 0 | 0 |  | 10343 | 10343 | 0.02302 |  |  | 10343 | 0.02302 | 2 | 438958.2836 | 449301.2836 | 1516150 | 0.70366 | stk added + 70% |  |  | 49922.3648 | 31768.7776 | 164 | Combined | 5852064.0305 | 5852064.0305 |  |  |  | N/A |  | 5852064.0305 |  |  |  | 5852064.0305 | 2 | 829 | 624903 | 14.1429 | 28.9505 | 0.081493 | 12211.0843 |  |  |  | 35186.076 | 8808.1714 | 5906.6561 | 25823.4127 | 263863.4048 | 26386.3405 | 365974.0616 | 86968.0688 | 18192.6041 | 105160.6729 | 288585.3446 | 393746.0175 | 759720.0791 | 187470.9 | 21468.9364 | 208939.8364 | 63096.4037 | 234082.5612 | 2 | 438958.2836 | 736137.2485 | 1495857.3276 |  | 166206.3697 | 105767.6898
|  |  | 8306-06-02 | Selective Catalytic Reduction (SCR) with ID fans | SCR |  | 1: 67; 33: #N/A; 45: 8306-06-02; 46: 2; 47: Selective Catalytic Reduction (SCR) with ID fans; 48: SCR; 49: 4 - Custom; 62: 2010-2009 average; 64: 0.1; 66: 14.99; 67: 14.99; 68: 14.9883; 71: 16.49; 72: 0.52382; 73: 0.52381; 74: 0.9; 78: 0.015842; 80: 4.95; 81: 44.55; 82: 0.9; 83: 0.90098; 84: 0.9; 85: 0.9; 86: Selective Catalytic Reduction (SCR) with ID fans; 88: 82710409; 89: 22170691; 90: 16807873; 91: 1261476; 92: 499178; 93: 1715272; 95: 838762; 97: 1048130; 104: 22170691; 123: 22170691; 124: 1; 125: 22170691; 126: 432189; 127: 37321875; 129: 37754064; 134: 588484; 135: 16615711; 136: 5581460; 137: 22785655; 146: 82710410; 149: 82710410; 150: 22170691; 151: 16807873; 152: 0.75811; 153: 4314688; 154: 0.19461; 155: 0; 156: 0; 157: 21122561; 158: 0.95272; 159: 1048130; 160: 0.047275; 161: 0; 162: 0; 163: 0; 164: 0; 165: 22170691; 168: 0; 169: 135187.1402; 170: 37754064; 171: 1.7029; 172: 22785655; 173: 1.0277; 174: 0.38024; 178: 82710410; 179: 82710410; 180: 1.209e-08; 181: 504331.7683; 182: 21346446; 183: 1294738; 184: 16.49; 185: 0.00017722; 188: 20000; 189: 62224; 190: 82224; 193: 21264222; 194: 21346446; 195: 20000; 196: 62224; 197: 82224; 200: 21264222; 201: 21346446; 202: 21346446; 203: 0; 205: 1294738; 206: 479157.037; 207: 4; 208: 22170691; 209: 0; 210: 0; 212: 22170691; 213: 135187.1402; 214: 37754064; 215: 22785655; 218: 0; 223: 82710410; 226: 82710410; 227: same TCC; 228: 504331.7683; 231: 20000; 232: 47.7954; 233: 62224; 234: 0.20758; 235: 82224; 236: 0; 237: 0; 238: 0; 240: 82224; 241: 82224; 242: 0.01308; 245: 82224; 246: 0.01308; 247: 2; 248: 6204036.63; 249: 6286260.63; 250: 21346446; 251: 0.70551; 252: stk added + 71%; 255: 381216.533; 256: 141105.738; 257: 164; 258: SCR; 259: 82710410; 260: 82710410; 264: 8609800; 265: 14894954; 266: 82710410; 270: 82710410; 271: 2; 272: 829; 273: 624903; 274: 44.55; 275: 28.9505; 276: 0.081493; 277: 12211.0843; 281: 35186.076; 282: 27745.74; 283: 18605.9668; 284: 25823.4127; 285: 263863.4048; 286: 26386.3405; 287: 397610.9408; 288: 86968.0688; 289: 46304.6882; 290: 133272.757; 291: 288585.3446; 292: 421858.1017; 293: 819469.0425; 294: 187470.9; 295: 21468.9364; 296: 208939.8364; 297: 79963.6542; 298: 595798.16; 299: 2; 300: 6204036.63; 301: 6879798.4442; 302: 7699267.4867; 304: 466905.2448; 305: 172823.0637
[7 empty] | 68 | [36 empty] | CAIR-OS (max last 3 yrs) | [197 empty] | 0
8306-07 | NRG | NH2 | 8306-07-01 | Separated Overfired Air / High Energy Reagent Technology (SOFA/HERT) | New Eqp |  | 69 | 7 |  |  |  | 8306-07 |  | NH2 | 1 |  | 172 |  | Utility Boiler | Combustion Engineering | Tangential fired |  |  |  | No. 6 oil | No. 2 oil |  |  | 0.21 |  | 48 hrs/year operation | [5 empty] | 2010-2009 average | 565.35 | 370125 | 370125 | 0.21 |  | 38.86 | CAIR-OS (max last 3 yrs) | 1523 | 1027131 | 0.15 |  | 76.7 |  | 8306-07-01 | 1 | Separated Overfired Air / High Energy Reagent Technology (SOFA/HERT) | New Eqp | 2 - Prog | [12 empty] | 2010-2009 average |  | 0.15 |  | 27.76 | 27.76 | 27.7594 |  |  | 11.1 | 0.28564 | 0.28571 | 0.45 |  |  |  | 0.082141 |  | 42.185 | 34.515 | 0.45 | 0.45239 | 0.45 | 0.45 | Separated Overfired Air / High Energy Reagent Technology (SOFA/HERT) |  | 5857063 | 1860912 | 1481238 | 50000 | 30000 | 100000 | [8 empty] | 100000 |  | 1661238 | 99674 | 1047639 | 500000 | 35000 | 20000 | 13339 | 370000 |  |  | 50000 | [6 empty] | 988339 | 59300 | 2908551 | 1 | 2908551 |  |  | 1308847.95 | 1308847.95 | 210869.9475 | 421739.895 | 210869.9475 |  |  |  |  | 843479.79 |  |  |  | 759131.811 | 32052.232 | 5000 |  |  | 5820010.551 |  |  | 5820010.551 | 2908551 | 1981238 | 0.68118 | 618339 | 0.21259 | 0 | 0 | 2599577 | 0.89377 | 50000 | 0.017191 | 0 | 0 | 100000 | 0.034381 | 2649577 | 158974 | 0.06 | 0 | 16910.1802 | 1308847.95 | 0.45 | 843479.79 | 0.29 | 0.2 | 759131.811 | 0.261 | 0.15 | 5820010.551 | 5857062.783 | -3.7046e-08 | 34052.6906 | 1516440 | 136570 | 11.1 | -0.00033841 |  |  | 5000 | 5633 | 10633 |  |  | 1505807 | 1516440 | 5000 | 5633 | 10633 |  |  | 1505807 | 1516440 | 1516440 | 0 |  | 136570 | 43935.6801 | 2 | 2649577 | 100000 | 0 | 158974.62 | 2908551.62 | 16910.1838 | 1308848.229 | 843479.9698 |  | 759131.9728 | 759131.9728 | 32052.2389 | 0 |  |  | 5852064.0305 |  |  | 5852064.0305 | stk added + 0% | 34023.6281 |  |  | 5000 | 8.8441 | 5633 | 0.015219 | 10633 | 0 | 0 | 0 |  | 10633 | 10633 | 0.02365 |  |  | 10633 | 0.02365 | 2 | 438958.2836 | 449591.2836 | 1516440 | 0.70352 | stk added + 70% |  |  | 40503.7192 | 13025.9679 | 172 | Combined | 5852064.0305 | 5852064.0305 |  |  |  | N/A |  | 5852064.0305 |  |  |  | 5852064.0305 | 2 | 1523 | 1027131 | 34.515 | 15.7584 | 0.10676 | 12806.747 |  |  |  | 64642.212 | 21495.942 | 14414.9258 | 35479.775 | 508404.2048 | 50840.4205 | 695277.4801 | 159773.6656 | 33422.6007 | 193196.2663 | 396498.449 | 589694.7153 | 1284972.1953 | 308139.3 | 22389.0961 | 330528.3961 | 115917.7598 | 234082.5612 | 2 | 438958.2836 | 788958.6046 | 2073930.7999 |  | 186840.6126 | 60087.8111
|  |  | 8306-07-02 | Selective Catalytic Reduction (SCR) with ID fans | SCR |  | 1: 70; 33: #N/A; 45: 8306-07-02; 46: 2; 47: Selective Catalytic Reduction (SCR) with ID fans; 48: SCR; 49: 4 - Custom; 62: 2010-2009 average; 64: 0.1; 66: 18.51; 67: 18.51; 68: 18.5063; 71: 20.35; 72: 0.52367; 73: 0.52381; 74: 0.9; 78: 0.014935; 80: 7.67; 81: 69.03; 82: 0.9; 83: 0.90043; 84: 0.9; 85: 0.9; 86: Selective Catalytic Reduction (SCR) with ID fans; 88: 82710409; 89: 22170691; 90: 16807873; 91: 1261476; 92: 499178; 93: 1715272; 95: 838762; 97: 1048130; 104: 22170691; 123: 22170691; 124: 1; 125: 22170691; 126: 432189; 127: 37321875; 129: 37754064; 134: 588484; 135: 16615711; 136: 5581460; 137: 22785655; 146: 82710410; 149: 82710410; 150: 22170691; 151: 16807873; 152: 0.75811; 153: 4314688; 154: 0.19461; 155: 0; 156: 0; 157: 21122561; 158: 0.95272; 159: 1048130; 160: 0.047275; 161: 0; 162: 0; 163: 0; 164: 0; 165: 22170691; 168: 0; 169: 128899.3663; 170: 37754064; 171: 1.7029; 172: 22785655; 173: 1.0277; 174: 0.38024; 178: 82710410; 179: 82710410; 180: 1.209e-08; 181: 480874.4767; 182: 21365116; 183: 1049528; 184: 20.35; 185: -0.0003381; 188: 20000; 189: 80894; 190: 100894; 193: 21264222; 194: 21365116; 195: 20000; 196: 80894; 197: 100894; 200: 21264222; 201: 21365116; 202: 21365116; 203: 0; 205: 1049528; 206: 309504.795; 207: 4; 208: 22170691; 209: 0; 210: 0; 212: 22170691; 213: 128899.3663; 214: 37754064; 215: 22785655; 218: 0; 223: 82710410; 226: 82710410; 227: same TCC; 228: 480874.4767; 231: 20000; 232: 35.3763; 233: 80894; 234: 0.21856; 235: 100894; 236: 0; 237: 0; 238: 0; 240: 100894; 241: 100894; 242: 0.016002; 245: 100894; 246: 0.016002; 247: 2; 248: 6204036.63; 249: 6304930.63; 250: 21365116; 251: 0.7049; 252: stk added + 70%; 255: 309824.601; 256: 91336.0949; 257: 172; 258: SCR; 259: 82710410; 260: 82710410; 264: 9007400; 265: 15582802; 266: 82710410; 270: 82710410; 271: 2; 272: 1523; 273: 1027131; 274: 69.03; 275: 15.7584; 276: 0.10676; 277: 12806.747; 281: 64642.212; 282: 42991.884; 283: 28829.8516; 284: 35479.775; 285: 508404.2048; 286: 50840.4205; 287: 731188.3479; 288: 159773.6656; 289: 88997.2779; 290: 248770.9435; 291: 396498.449; 292: 645269.3925; 293: 1376457.7404; 294: 308139.3; 295: 22389.0961; 296: 330528.3961; 297: 149262.5661; 298: 623312.08; 299: 2; 300: 6204036.63; 301: 6976611.2761; 302: 8353069.0165; 304: 410470.2219; 305: 121006.3598
[7 empty] | 71 | [36 empty] | CAIR-OS (max last 3 yrs) | [197 empty] | 0
8305-01 | PSEG | NHB1 | 8305-01-01 | Low NOx Burners (LNB) | New Eqp |  | 1: 72; 2: 8; 3: 5; 4: PSEG Power LLC, PSEG Fossil LLC, PSEG Power Connecticut; 5: 8305; 6: 8305-01; 7: New Haven Harbor; 8: NHB1; 9: 1; 11: Unit is a steam boiler, only; 13: Utility Boiler; 14: Not Known; 17: 1975; 18: 52 yrs; 19: No. 6 oil; 21: 0.4; 23: 0.4; 25: 48 hrs/year operation; 31: 2010-2009 average; 35: 0.4; 38: CAIR-OS (max last 3 yrs); 39: 849; 40: 1485780; 41: 0.14; 43: 102; 45: 8305-01-01; 46: 1; 47: Low NOx Burners (LNB); 48: New Eqp; 49: 4 - Custom; 74: 0.3; 78: 0.096111; 80: 71.4; 81: 30.6; 82: 0.3; 83: 0.31349; 84: 0.3; 85: 0.3; 86: Low NOx Burners (LNB); 88: 133450; 89: 133450; 90: 133450; 91: 0; 104: 133450; 123: 133450; 124: 1; 125: 133450; 129: 0; 137: 0; 141: 0; 146: 133450; 149: 133450; 150: 133450; 151: 133450; 152: 1; 153: 0; 154: 0; 155: 0; 156: 0; 157: 133450; 158: 1; 159: 0; 160: 0; 161: 0; 162: 0; 163: 0; 164: 0; 165: 133450; 168: 0; 169: 133450; 170: 0; 171: 0; 172: 0; 173: 0; 174: 0; 175: 0; 176: 0; 177: 0; 178: 133450; 179: 133450; 180: 0; 183: 4448; 184: 1; 194: 4448; 202: 4448; 205: 4448; 208: 133450; 209: 0; 210: 0; 212: 133450; 218: 0; 223: 133450; 226: 133450; 227: same TCC; 236: 0; 238: 0; 247: 2; 248: 10009.9696; 249: 10009.9696; 250: 4448; 251: -1.2504; 252: -1.2504; 256: 327.1232; 258: Other; 259: 133450; 260: 133450; 264: N/A; 266: 133450; 270: 133450; 271: 2; 272: 849; 273: 1485780; 274: 30.6; 275: 28.2686; 276: 0.08213; 277: 0; 281: 36034.956; 282: 19057.68; 283: 12779.856; 284: 0; 285: 0; 286: 0; 287: 67872.492; 288: 89066.2128; 289: 424.8714; 290: 89491.0842; 291: 0; 292: 89491.0842; 293: 157363.5762; 294: 445734; 295: 21504.2796; 296: 467238.2796; 297: 53694.6505; 298: 5338; 299: 2; 300: 10009.9696; 301: 69042.6201; 302: 226406.1964; 305: 7398.8953
|  |  | 8305-01-02 | Flue Gas Recirculation (FGR) | New Eqp |  | 1: 73; 33: #N/A; 45: 8305-01-02; 46: 2; 47: Flue Gas Recirculation (FGR); 48: New Eqp; 49: 4 - Custom; 71: 3.5234; 74: 0.3; 78: 0.096111; 80: 71.4; 81: 30.6; 82: 0.3; 83: 0.31349; 84: 0.3; 85: 0.3; 86: Flue Gas Recirculation (FGR); 88: 101676; 89: 101676; 90: 101676; 91: 0; 104: 101676; 123: 101676; 124: 1; 125: 101676; 129: 0; 137: 0; 141: 0; 146: 101676; 149: 101676; 150: 101676; 151: 101676; 152: 1; 153: 0; 154: 0; 155: 0; 156: 0; 157: 101676; 158: 1; 159: 0; 160: 0; 161: 0; 162: 0; 163: 0; 164: 0; 165: 101676; 168: 0; 169: 101676; 170: 0; 171: 0; 172: 0; 173: 0; 174: 0; 175: 0; 176: 0; 177: 0; 178: 101676; 179: 101676; 180: 0; 182: 9855; 183: 2797; 184: 3.5234; 185: 0; 194: 9855; 202: 9855; 205: 2797; 208: 101676; 209: 0; 210: 0; 212: 101676; 218: 0; 223: 101676; 226: 101676; 227: same TCC; 236: 0; 238: 0; 247: 2; 248: 7626.6292; 249: 7626.6292; 250: 9855; 251: 0.22612; 252: stk added + 23%; 255: 2164.5542; 256: 249.2362; 258: Other; 259: 101676; 260: 101676; 264: N/A; 266: 101676; 270: 101676; 271: 2; 272: 849; 273: 1485780; 274: 30.6; 275: 28.2686; 276: 0.08213; 277: 0; 281: 36034.956; 282: 19057.68; 283: 12779.856; 284: 0; 285: 0; 286: 0; 287: 67872.492; 288: 89066.2128; 289: 323.711; 290: 89389.9238; 291: 0; 292: 89389.9238; 293: 157262.4158; 294: 445734; 295: 21504.2796; 296: 467238.2796; 297: 53633.9543; 298: 4067.04; 299: 2; 300: 7626.6292; 301: 65327.6235; 302: 222590.0392; 304: 63174.4637; 305: 7274.1843
[7 empty] | 74 | [36 empty] | CAIR-OS (max last 3 yrs) | [197 empty] | 0
8305-02 | PSEG | BHB2 | 8305-02-01 | Selective Catalytic Reduction (SCR) | SCR |  | 1: 75; 2: 9; 6: 8305-02; 7: Bridgeport Harbor Station; 8: BHB2; 9: 1; 11: 170; 12: 602; 13: Utility Boiler; 14: Babcock and Wilcox; 17: Aug 1961; 18: 66 yrs; 19: No. 6 oil; 20: No. 2 oil; 25: 48 hrs/year operation; 31: 2010-2009 average; 38: CAIR-OS (max last 3 yrs); 39: 122; 40: 85201; 41: 0.28; 43: 11.8; 45: 8305-02-01; 46: 1; 47: Selective Catalytic Reduction (SCR); 48: SCR; 49: 4 - Custom; 71: 2.0555; 74: 0.9; 78: 0.027699; 80: 1.18; 81: 10.62; 82: 0.9; 83: 0.90107; 84: 0.9; 85: 0.9; 86: Selective Catalytic Reduction (SCR); 88: 17483068; 89: 17483068; 90: 17483068; 91: 0; 104: 17483068; 123: 17483068; 124: 1; 125: 17483068; 129: 0; 137: 0; 141: 0; 146: 17483068; 149: 17483068; 150: 17483068; 151: 17483068; 152: 1; 153: 0; 154: 0; 155: 0; 156: 0; 157: 17483068; 158: 1; 159: 0; 160: 0; 161: 0; 162: 0; 163: 0; 164: 0; 165: 17483068; 168: 0; 169: 102841.5765; 170: 0; 171: 0; 172: 0; 173: 0; 174: 0; 175: 0; 176: 0; 177: 0; 178: 17483068; 179: 17483068; 180: 0; 181: 102841.5765; 182: 596854; 183: 290373; 184: 2.0555; 185: 0; 194: 596854; 202: 596854; 205: 290373; 208: 17483068; 209: 0; 210: 0; 212: 17483068; 213: 102841.5765; 218: 0; 223: 17483068; 226: 17483068; 227: same TCC; 228: 102841.5765; 236: 0; 238: 0; 247: 2; 248: 1311389.8755; 249: 1311389.8755; 250: 596854; 251: -1.1972; 252: -1.1972; 255: 637998.9283; 256: 123483.0391; 257: 170; 258: SCR; 259: 17483068; 260: 17483068; 264: 8908000; 265: 15410840; 266: 17483068; 270: 17483068; 271: 2; 272: 122; 273: 85201; 274: 10.62; 275: 196.7213; 276: 0.07; 277: 12657.8313; 281: 5178.168; 282: 6614.136; 283: 4435.3618; 284: 22992.9887; 285: 40252.192; 286: 4025.2192; 287: 83498.0657; 288: 12798.6784; 289: 7050.4593; 290: 19849.1377; 292: 19849.1377; 293: 103347.2034; 294: 25560.3; 295: 18810.013; 296: 44370.313; 297: 11909.4826; 298: 616433.6; 299: 2; 300: 1311389.8755; 301: 1939732.9582; 302: 2043080.1616; 304: 993970.5787; 305: 192380.4295
|  |  | 8305-02-02 | Combination of Control Technologies LNB + OFA + SNCR | New Eqp |  | 1: 76; 33: #N/A; 45: 8305-02-02; 46: 2; 47: Combination of Control Technologies LNB + OFA + SNCR; 48: New Eqp; 49: 4 - Custom; 71: 1.9925; 74: 0.45; 78: 0.15235; 80: 6.49; 81: 5.31; 82: 0.45; 83: 0.45591; 84: 0.45; 85: 0.45; 86: Combination of Control Technologies LNB + OFA + SNCR; 88: 5537165; 89: 5537165; 90: 5537165; 91: 0; 104: 5537165; 123: 5537165; 124: 1; 125: 5537165; 129: 0; 137: 0; 141: 0; 146: 5537165; 149: 5537165; 150: 5537165; 151: 5537165; 152: 1; 153: 0; 154: 0; 155: 0; 156: 0; 157: 5537165; 158: 1; 159: 0; 160: 0; 161: 0; 162: 0; 163: 0; 164: 0; 165: 5537165; 168: 0; 169: 32571.5588; 170: 0; 171: 0; 172: 0; 173: 0; 174: 0; 175: 0; 176: 0; 177: 0; 178: 5537165; 179: 5537165; 180: 0; 181: 32571.5588; 182: 391715; 183: 196596; 184: 1.9925; 185: 0; 194: 391715; 202: 391715; 205: 196596; 208: 5537165; 209: 0; 210: 0; 212: 5537165; 213: 32571.5588; 218: 0; 223: 5537165; 226: 5537165; 227: same TCC; 228: 32571.5588; 236: 0; 238: 0; 247: 2; 248: 415337.9785; 249: 415337.9785; 250: 391715; 251: -0.060307; 252: -0.060307; 255: 208452.0256; 256: 78218.075; 257: 170; 258: Combined; 259: 5537165; 260: 5537165; 264: N/A; 266: 5537165; 270: 5537165; 271: 2; 272: 122; 273: 85201; 274: 5.31; 275: 196.7213; 276: 0.07; 277: 12657.8313; 281: 5178.168; 282: 3307.068; 283: 2217.6809; 284: 22992.9887; 285: 40252.192; 286: 4025.2192; 287: 77973.3168; 288: 12798.6784; 289: 2533.253; 290: 15331.9314; 292: 15331.9314; 293: 93305.2482; 294: 25560.3; 295: 18810.013; 296: 44370.313; 297: 9199.1588; 298: 221486.6; 299: 2; 300: 415337.9785; 301: 646023.7373; 302: 739328.9855; 304: 371058.3491; 305: 139233.3306
|  |  | 8305-02-03 | Combination of Control Technologies LNB + OFA + FGR | New Eqp |  | 1: 77; 33: #N/A; 45: 8305-02-03; 46: 3; 47: Combination of Control Technologies LNB + OFA + FGR; 48: New Eqp; 49: 4 - Custom; 71: 1.0001; 74: 0.45; 78: 0.15235; 80: 6.49; 81: 5.31; 82: 0.45; 83: 0.45591; 84: 0.45; 85: 0.45; 86: Combination of Control Technologies LNB + OFA + FGR; 88: 4271527; 89: 4271527; 90: 4271527; 91: 0; 104: 4271527; 123: 4271527; 124: 1; 125: 4271527; 129: 0; 137: 0; 141: 0; 146: 4271527; 149: 4271527; 150: 4271527; 151: 4271527; 152: 1; 153: 0; 154: 0; 155: 0; 156: 0; 157: 4271527; 158: 1; 159: 0; 160: 0; 161: 0; 162: 0; 163: 0; 164: 0; 165: 4271527; 168: 0; 169: 25126.6294; 170: 0; 171: 0; 172: 0; 173: 0; 175: 0; 176: 0; 178: 4271527; 179: 4271527; 180: 0; 181: 25126.6294; 182: 122675; 183: 122660; 184: 1.0001; 185: 0; 194: 122675; 202: 122675; 205: 122660; 208: 4271527; 209: 0; 210: 0; 212: 4271527; 213: 25126.6294; 218: 0; 223: 4271527; 226: 4271527; 227: same TCC; 228: 25126.6294; 236: 0; 238: 0; 247: 2; 248: 320403.5619; 249: 320403.5619; 250: 122675; 251: -1.6118; 252: -1.6118; 255: 320364.3848; 256: 60339.6539; 257: 170; 258: Combined; 259: 4271527; 260: 4271527; 264: N/A; 266: 4271527; 270: 4271527; 271: 2; 272: 122; 273: 85201; 274: 5.31; 275: 196.7213; 276: 0.07; 277: 12657.8313; 281: 5178.168; 282: 3307.068; 283: 2217.6809; 284: 22992.9887; 285: 40252.192; 286: 4025.2192; 287: 77973.3168; 288: 12798.6784; 289: 1954.2236; 290: 14752.902; 292: 14752.902; 293: 92726.2188; 294: 25560.3; 295: 18810.013; 296: 44370.313; 297: 8851.7412; 298: 170861.08; 299: 2; 300: 320403.5619; 301: 500116.3831; 302: 592842.602; 304: 592770.1126; 305: 111646.441
[7 empty] | 78 | [36 empty] | CAIR-OS (max last 3 yrs) | [197 empty] | 0
8305-03 | PSEG | BHB3 | 8305-03-01 | Work in progress, PSEG asks for more time to develop a solution, due to limited information on the NOx control technologies feasibility on coal boliers |  |  | 1: 79; 2: 10; 6: 8305-03; 8: BHB3; 9: 1; 11: 410; 13: Utility Boiler; 14: Combustion Engineering; 17: Aug 1968; 18: 58 yrs; 19: Coal; 20: No. 6 oil; 25: 48 hrs/year operation; 31: 2010-2009 average; 38: CAIR-OS (max last 3 yrs); 39: 3474; 40: 13163750; 41: 0.14; 43: 916.7; 45: 8305-03-01; 46: 1; 47: Work in progress, PSEG asks for more time to develop a solution, due to limited information on the NOx control technologies feasibility on coal boliers; 49: 4 - Custom; 74: 0.6; 78: 0.055711; 80: 366.68; 81: 550.02; 82: 0.6; 83: 0.60207; 84: 0.6; 85: 0.6; 86: Work in progress, PSEG asks for more time to develop a solution, due to limited information on the NOx control technologies feasibility on coal boliers; 146: 0; 149: 0; 155: 0; 178: 0; 179: 0; 181: 0; 236: 0; 247: 2; 257: 410; 258: Other; 259: 0; 260: 0; 264: N/A; 266: 0; 270: 0; 272: 3474; 273: 13163750; 274: 550.02; 281: 147450.456; 287: 147450.456; 288: 364447.6128; 289: 0; 290: 364447.6128; 292: 364447.6128; 293: 511898.0688; 296: 0; 298: 0; 299: 2; 300: 0; 301: 0; 302: 0; 305: 0
80
▲
Ref for PSEG 8305 is J95

## A1(epa)
[5 empty] | 1 | To see "Unit CAIROS Emissions Report - ozone season" go to row 7 or click on # 1 on the left
[5 empty] | 2 | To see "Unit CAIROS Emissions Report - whole year" go to row 220 below
x
Unit CAIROS Emissions Report - Ozone Season
40773
Your query will return data for 27 facilities and 68 units.
You specified: Ozone Season(s): 2010,2009,2008 Program: CAIROS State(s): CT
|  |  |  | No. | Seq | Unit No. | TA&O #adj | TA&O | Rnk | TA&O ID | Unit ID | State | Facility Name | Permit # | Facility ID (ORISPL) | Unit ID | Associated Stacks | Year | Program(s) | Operating Time | # of Months Reported | Gross Load (MWh) | Steam Load (1000 lb) | Avg. NOx Rate (lb/mmBtu) | NOx Tons | Heat Input (mmBtu) | EGU/Non EGU | Source Category | SIC Code | SIC Code Description | Owner/Operator Name (Type) | Operator Name (Type) | Representative (Primary) | Representative (Alternate) | SO2 Phase | NOx Phase | Operating Status | Unit Type | Fuel Type(s) (Primary) | Fuel Type(s) (Secondary) | SO2 Control(s) | NOx Control(s) (1) | NOx Control(s) (2) | NOx Control(s) (3) | PM Control(s) | Maximum Heat Input Capacity
REFERENCE ID |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43
#N/A |  |  |  | 1 | 3 | 1 |  | #N/A |  | #N/A | #N/A | CT | AES Thames |  | 10675 | UNITA | CS01 | 2010 | CAIROS | 3657 | 5 |  | 2549454 | 0.05 | 95.9 | 3596311 | EGU | Cogeneration | 4961 | Steam Supply | AES Corporation (Owner/Operator) | [5 empty] | Operating | Circulating fluidized bed boiler | Coal |  | Fluidized Bed Limestone Injection | Other |  |  | Baghouse | 1045
#N/A |  |  |  | 2 | 2 |  |  | #N/A |  | #N/A | #N/A | CT | AES Thames |  | 10675 | UNITA | CS01 | 2009 | CAIROS | 3664 | 5 |  | 2613827 | 0.05 | 90 | 3476023 | EGU | Cogeneration | 4961 | Steam Supply | AES Corporation (Owner/Operator) | [5 empty] | Operating | Circulating fluidized bed boiler | Coal |  | Fluidized Bed Limestone Injection | Other |  |  | Baghouse | 1045
#N/A |  |  |  | 3 | 1 |  |  | #N/A |  | #N/A | #N/A | CT | AES Thames |  | 10675 | UNITA | CS01 | 2008 | CAIROS | 3672 | 5 |  | 2613333 | 0.04 | 68.3 | 3586223 | EGU | Cogeneration | 4961 | Steam Supply | AES Corporation (Owner/Operator) | [5 empty] | Operating | Circulating fluidized bed boiler | Coal |  | Fluidized Bed Limestone Injection | Other |  |  | Baghouse | 1045
#N/A |  |  |  | 4 | 6 | 2 |  | #N/A |  | #N/A | #N/A | CT | AES Thames |  | 10675 | UNITB | CS01 | 2010 | CAIROS | 3472 | 5 |  | 2413682 | 0.05 | 88.1 | 3404517 | EGU | Cogeneration | 4961 | Steam Supply | AES Corporation (Owner/Operator) | [5 empty] | Operating | Circulating fluidized bed boiler | Coal |  | Fluidized Bed Limestone Injection | Other |  |  | Baghouse | 1045
#N/A |  |  |  | 5 | 5 |  |  | #N/A |  | #N/A | #N/A | CT | AES Thames |  | 10675 | UNITB | CS01 | 2009 | CAIROS | 3538 | 5 |  | 2512118 | 0.05 | 85.4 | 3343742 | EGU | Cogeneration | 4961 | Steam Supply | AES Corporation (Owner/Operator) | [5 empty] | Operating | Circulating fluidized bed boiler | Coal |  | Fluidized Bed Limestone Injection | Other |  |  | Baghouse | 1045
#N/A |  |  |  | 6 | 4 |  |  | #N/A |  | #N/A | #N/A | CT | AES Thames |  | 10675 | UNITB | CS01 | 2008 | CAIROS | 3672 | 5 |  | 2615702 | 0.04 | 68.3 | 3589512 | EGU | Cogeneration | 4961 | Steam Supply | AES Corporation (Owner/Operator) | [5 empty] | Operating | Circulating fluidized bed boiler | Coal |  | Fluidized Bed Limestone Injection | Other |  |  | Baghouse | 1045
#N/A |  |  |  | 7 | 11 | 3 |  | #N/A |  | #N/A | #N/A | CT | Alfred L Pierce Generating Station |  | 6635 | AP-1 |  | 2010 | CAIROS | 35 | 5 | 2256 |  | 0.09 | 1.3 | 32767 | EGU | Electric Utility |  |  | Connecticut Municipal Electric Energy Coop (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combustion turbine | Pipeline Natural Gas | Diesel Oil |  | Dry Low NOx Burner | Water Injection |  |  | 1560
#N/A |  |  |  | 8 | 9 |  |  | #N/A |  | #N/A | #N/A | CT | Alfred L Pierce Generating Station |  | 6635 | AP-1 |  | 2009 | CAIROS | 18 | 5 | 1274 |  | 0.09 | 1.2 | 22712 | EGU | Electric Utility |  |  | Connecticut Municipal Electric Energy Coop (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combustion turbine | Pipeline Natural Gas | Diesel Oil |  | Dry Low NOx Burner | Water Injection |  |  | 1560
#N/A |  |  |  | 9 | 7 |  |  | #N/A |  | #N/A | #N/A | CT | Alfred L Pierce Generating Station |  | 6635 | AP-1 |  | 2008 | CAIROS | 19 | 5 | 1073 |  | 0.09 | 0.6 | 14217 | EGU | Electric Utility |  |  | Connecticut Municipal Electric Energy Coop (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combustion turbine | Pipeline Natural Gas | Diesel Oil |  | Dry Low NOx Burner | Water Injection |  |  | 1560
#N/A |  |  |  | 10 | 15 | 4 |  | #N/A |  | #N/A | #N/A | CT | Algonquin Power Windsor Locks, LLC |  | 10567 | GT1 |  | 2010 | CAIROS | 3672 | 5 | 92057 |  | 0.14 | 82.9 | 1222779 | EGU | Cogeneration | 4911 | Electric Services | Algonquin Power Windsor Locks, LLC (Owner/Operator) | [5 empty] | Operating | Combined cycle | Pipeline Natural Gas | Residual Oil |  | Steam Injection |  |  |  | 555
#N/A |  |  |  | 11 | 14 |  |  | #N/A |  | #N/A | #N/A | CT | Algonquin Power Windsor Locks, LLC |  | 10567 | GT1 |  | 2009 | CAIROS | 3666 | 5 | 126060 |  | 0.14 | 105.6 | 1531598 | EGU | Cogeneration | 4911 | Electric Services | Algonquin Power Windsor Locks, LLC (Owner/Operator) | [5 empty] | Operating | Combined cycle | Pipeline Natural Gas | Residual Oil |  | Steam Injection |  |  |  | 555
#N/A |  |  |  | 12 | 13 |  |  | #N/A |  | #N/A | #N/A | CT | Algonquin Power Windsor Locks, LLC |  | 10567 | GT1 |  | 2008 | CAIROS | 3672 | 5 | 130472 |  | 0.14 | 107.8 | 1550997 | EGU | Cogeneration | 4911 | Electric Services | Algonquin Power Windsor Locks, LLC (Owner/Operator) | [5 empty] | Operating | Combined cycle | Pipeline Natural Gas | Residual Oil |  | Steam Injection |  |  |  | 555
8300-01 | NRG | BR10 |  | 13 | 18 | 5 |  | 8300 | 1 | 8300-01 | BR10 | CT | Branford |  | 540 | 10 |  | 2010 | CAIROS | 39 | 5 | 512 |  | 1.2 | 5.9 | 9750 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Other Oil |  |  | Water Injection |  |  |  | 250
|  |  |  | 14 | 17 | [6 empty] | CT | Branford |  | 540 | 10 |  | 2009 | CAIROS | 2 | 5 | 20 |  | 1.2 | 0.3 | 525 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Other Oil |  |  | Water Injection |  |  |  | 250
|  |  |  | 15 | 16 | [6 empty] | CT | Branford |  | 540 | 10 |  | 2008 | CAIROS | 7 | 5 | 123 |  | 1.2 | 1.1 | 1778 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Other Oil |  |  | Water Injection (Began Jun 01, 2008) |  |  |  | 250
#N/A |  |  |  | 16 | 21 | 6 |  | #N/A |  | #N/A | #N/A | CT | Bridgeport Energy |  | 55042 | BE1 |  | 2010 | CAIROS | 3338 | 5 | 502693 |  | 0.02 | 42.4 | 5399353 | EGU | Electric Utility | 4911 | Electric Services | Bridgeport Energy, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combined cycle | Pipeline Natural Gas |  |  | Selective Catalytic Reduction |  |  |  | 1884
#N/A |  |  |  | 17 | 20 |  |  | #N/A |  | #N/A | #N/A | CT | Bridgeport Energy |  | 55042 | BE1 |  | 2009 | CAIROS | 3055 | 5 | 429466 |  | 0.02 | 34.3 | 4640621 | EGU | Electric Utility | 4911 | Electric Services | Bridgeport Energy, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combined cycle | Pipeline Natural Gas |  |  | Selective Catalytic Reduction |  |  |  | 1884
#N/A |  |  |  | 18 | 19 |  |  | #N/A |  | #N/A | #N/A | CT | Bridgeport Energy |  | 55042 | BE1 |  | 2008 | CAIROS | 2602 | 5 | 339851 |  | 0.02 | 32.6 | 3739477 | EGU | Electric Utility | 4911 | Electric Services | Bridgeport Energy, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combined cycle | Pipeline Natural Gas |  |  | Selective Catalytic Reduction |  |  |  | 1884
#N/A |  |  |  | 19 | 24 | 7 |  | #N/A |  | #N/A | #N/A | CT | Bridgeport Energy |  | 55042 | BE2 |  | 2010 | CAIROS | 3165 | 5 | 475224 |  | 0.02 | 39.5 | 5058494 | EGU | Electric Utility | 4911 | Electric Services | Bridgeport Energy, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combined cycle | Pipeline Natural Gas |  |  | Selective Catalytic Reduction |  |  |  | 1884
#N/A |  |  |  | 20 | 23 |  |  | #N/A |  | #N/A | #N/A | CT | Bridgeport Energy |  | 55042 | BE2 |  | 2009 | CAIROS | 2942 | 5 | 417769 |  | 0.02 | 35.7 | 4463492 | EGU | Electric Utility | 4911 | Electric Services | Bridgeport Energy, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combined cycle | Pipeline Natural Gas |  |  | Selective Catalytic Reduction |  |  |  | 1884
#N/A |  |  |  | 21 | 22 |  |  | #N/A |  | #N/A | #N/A | CT | Bridgeport Energy |  | 55042 | BE2 |  | 2008 | CAIROS | 2761 | 5 | 365520 |  | 0.02 | 34.2 | 4009046 | EGU | Electric Utility | 4911 | Electric Services | Bridgeport Energy, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combined cycle | Pipeline Natural Gas |  |  | Selective Catalytic Reduction |  |  |  | 1884
|  |  |  | 22 | 25 | 8 | NA |  |  |  |  | CT | Bridgeport Harbor Station |  | 568 | BHB1 |  | 2008 | CAIROS | 0 | 5 | [5 empty] | EGU | Electric Utility | 4911 | Electric Services | PSEG (Owner/Operator) (Started Jul 28, 2008) |  |  |  | Phase 2 |  | Operating | Cyclone boiler | Residual Oil | Diesel Oil |  |  |  |  | Electrostatic Precipitator | 865
8305-02 | PSEG | BHB2 |  | 23 | 32 | 9 | 4 | 8305 | 2 | 8305-02 | BHB2 | CT | Bridgeport Harbor Station |  | 568 | BHB2 |  | 2010 | CAIROS | 122 | 5 | 6954 |  | 0.24 | 11.8 | 85201 | EGU | Electric Utility | 4911 | Electric Services | PSEG Power Connecticut, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Cyclone boiler | Residual Oil | Diesel Oil |  |  |  |  | Electrostatic Precipitator | 1785
|  |  |  | 24 | 29 |  | 4 | 8305 | 2 | 8305-02 | BHB2 | CT | Bridgeport Harbor Station |  | 568 | BHB2 |  | 2009 | CAIROS | 64 | 5 | 3168 |  | 0.2 | 5.4 | 39994 | EGU | Electric Utility | 4911 | Electric Services | PSEG Power Connecticut, LLC (Owner/Operator) (Started Oct 14, 2009) |  |  |  | Phase 2 |  | Operating | Cyclone boiler | Residual Oil | Diesel Oil |  |  |  |  | Electrostatic Precipitator | 1785
|  |  |  | 25 | 27 |  | 4 | 8305 | 2 | 8305-02 | BHB2 | CT | Bridgeport Harbor Station |  | 568 | BHB2 |  | 2008 | CAIROS | 152 | 5 | 6521 |  | 0.18 | 11.3 | 78403 | EGU | Electric Utility | 4911 | Electric Services | PSEG (Owner/Operator) (Started Jul 28, 2008) |  |  |  | Phase 2 |  | Operating | Cyclone boiler | Residual Oil | Diesel Oil |  |  |  |  | Electrostatic Precipitator | 1785
8305-03 | PSEG | BHB3 |  | 26 | 38 | 10 | 4 | 8305 | 3 | 8305-03 | BHB3 | CT | Bridgeport Harbor Station |  | 568 | BHB3 |  | 2010 | CAIROS | 2522 | 5 | 678834 |  | 0.14 | 500.5 | 6920835 | EGU | Electric Utility | 4911 | Electric Services | PSEG Power Connecticut, LLC (Owner/Operator) |  |  |  | Phase 2 | Early Election | Operating | Tangentially-fired | Coal | Diesel Oil, Residual Oil |  | Low NOx Burner Technology w/ Separated OFA |  |  | Electrostatic Precipitator | 4100
8305-03 |  |  |  | 27 | 35 |  | 4 | 8305 | 3 | 8305-03 | BHB3 | CT | Bridgeport Harbor Station |  | 568 | BHB3 |  | 2009 | CAIROS | 556 | 5 | 129134 |  | 0.15 | 109.5 | 1410547 | EGU | Electric Utility | 4911 | Electric Services | PSEG Power Connecticut, LLC (Owner/Operator) (Started Oct 14, 2009) |  |  |  | Phase 2 | Early Election | Operating | Tangentially-fired | Coal | Diesel Oil, Residual Oil |  | Low NOx Burner Technology w/ Separated OFA |  |  | Electrostatic Precipitator | 4100
8305-03 |  |  |  | 28 | 33 |  | 4 | 8305 | 3 | 8305-03 | BHB3 | CT | Bridgeport Harbor Station |  | 568 | BHB3 |  | 2008 | CAIROS | 3474 | 5 | 1293218 |  | 0.14 | 916.7 | 13163750 | EGU | Electric Utility | 4911 | Electric Services | PSEG (Owner/Operator) (Started Jul 28, 2008) |  |  |  | Phase 2 | Early Election | Operating | Tangentially-fired | Coal | Diesel Oil, Residual Oil |  | Low NOx Burner Technology w/ Separated OFA |  |  | Electrostatic Precipitator | 4100
8301-01 | PSEG | BHB4 |  | 29 | 44 | 11 |  | 8301 | 1 | 8301-01 | BHB4 | CT | Bridgeport Harbor Station |  | 568 | BHB4 |  | 2010 | CAIROS | 11 | 5 | 114 |  | 0.71 | 0.7 | 2026 | EGU | Electric Utility | 4911 | Electric Services | PSEG Power Connecticut, LLC (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Other Oil | [6 empty] | 287
8301-01 |  |  |  | 30 | 41 |  |  | 8301 | 1 | 8301-01 | BHB4 | CT | Bridgeport Harbor Station |  | 568 | BHB4 |  | 2009 | CAIROS | 8 | 5 | 119 |  | 0.67 | 0.7 | 1962 | EGU | Electric Utility | 4911 | Electric Services | PSEG Power Connecticut, LLC (Owner/Operator) (Started Oct 14, 2009) | [5 empty] | Operating | Combustion turbine | Other Oil | [6 empty] | 287
8301-01 |  |  |  | 31 | 39 |  |  | 8301 | 1 | 8301-01 | BHB4 | CT | Bridgeport Harbor Station |  | 568 | BHB4 |  | 2008 | CAIROS | 24 | 5 | 105 |  | 0.67 | 0.8 | 2366 | EGU | Electric Utility | 4911 | Electric Services | PSEG (Owner/Operator) (Started Jul 28, 2008) | [5 empty] | Operating | Combustion turbine | Other Oil | [6 empty] | 287
8298-01 | CDECCA | GT |  | 32 | 51 | 12 |  | 8298 | 1 | 8298-01 | GT | CT | Capitol District Energy Center |  | 50498 | GT |  | 2010 | CAIROS | 229 | 5 | 8884 |  | 0.12 | 4.2 | 79936 | EGU | Cogeneration | 4961 | Steam Supply | Capitol District Energy Center Cogeneration Assoc. (Owner) / PurEnergy, LLC (Operator) |  |  |  | Phase 2 |  | Operating | Combined cycle | Pipeline Natural Gas | Diesel Oil | [5 empty] | 739
8298-01 |  |  |  | 33 | 49 |  |  | 8298 | 1 | 8298-01 | GT | CT | Capitol District Energy Center |  | 50498 | GT |  | 2009 | CAIROS | 152 | 5 | 5669 |  | 0.12 | 2.7 | 49960 | EGU | Cogeneration | 4961 | Steam Supply | Capitol District Energy Center Cogeneration Assoc. (Owner / PurEnergy, LLC (Operator) |  |  |  | Phase 2 |  | Operating | Combined cycle | Pipeline Natural Gas | Diesel Oil | [5 empty] | 739
8298-01 |  |  |  | 34 | 45 |  |  | 8298 | 1 | 8298-01 | GT | CT | Capitol District Energy Center |  | 50498 | GT |  | 2008 | CAIROS | 324 | 5 | 14379 |  | 0.12 | 7.2 | 128717 | EGU | Cogeneration | 4961 | Steam Supply | Capitol District Energy Center Cogeneration Assoc. (Owner) / PurEnergy, LLC (Operator) |  |  |  | Phase 2 |  | Operating | Combined cycle | Pipeline Natural Gas | Diesel Oil | [5 empty] | 739
8300-02 | NRG | CC10 |  | 35 | 55 | 13 |  | 8300 | 2 | 8300-02 | CC10 | CT | Cos Cob |  | 542 | 10 |  | 2010 | CAIROS | 44 | 5 | 677 |  | 1.2 | 6.6 | 11038 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Other Oil |  |  | Water Injection |  |  |  | 250
8300-02 |  |  |  | 36 | 54 |  |  | 8300 | 2 | 8300-02 | CC10 | CT | Cos Cob |  | 542 | 10 |  | 2009 | CAIROS | 8 | 5 | 139 |  | 1.2 | 1.2 | 1968 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Other Oil |  |  | Water Injection |  |  |  | 250
8300-02 |  |  |  | 37 | 53 |  |  | 8300 | 2 | 8300-02 | CC10 | CT | Cos Cob |  | 542 | 10 |  | 2008 | CAIROS | 11 | 5 | 183 |  | 1.2 | 1.6 | 2740 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Other Oil |  |  | Water Injection (Began Jul 01, 2008) |  |  |  | 250
8300-03 | NRG | CC11 |  | 38 | 58 | 14 |  | 8300 | 3 | 8300-03 | CC11 | CT | Cos Cob |  | 542 | 11 |  | 2010 | CAIROS | 40 | 5 | 619 |  | 1.2 | 6.1 | 10085 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Other Oil |  |  | Water Injection |  |  |  | 250
8300-03 |  |  |  | 39 | 57 |  |  | 8300 | 3 | 8300-03 | CC11 | CT | Cos Cob |  | 542 | 11 |  | 2009 | CAIROS | 6 | 5 | 102 |  | 1.2 | 0.9 | 1465 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Other Oil |  |  | Water Injection |  |  |  | 250
8300-03 |  |  |  | 40 | 56 |  |  | 8300 | 3 | 8300-03 | CC11 | CT | Cos Cob |  | 542 | 11 |  | 2008 | CAIROS | 9 | 5 | 160 |  | 1.2 | 1.3 | 2225 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Other Oil |  |  | Water Injection (Began Jul 01, 2008) |  |  |  | 250
8300-04 | NRG | CC12 |  | 41 | 61 | 15 |  | 8300 | 4 | 8300-04 | CC12 | CT | Cos Cob |  | 542 | 12 |  | 2010 | CAIROS | 51 | 5 | 790 |  | 1.2 | 7.7 | 12848 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Other Oil |  |  | Water Injection |  |  |  | 250
8300-04 |  |  |  | 42 | 60 |  |  | 8300 | 4 | 8300-04 | CC12 | CT | Cos Cob |  | 542 | 12 |  | 2009 | CAIROS | 7 | 5 | 131 |  | 1.2 | 1.1 | 1780 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Other Oil |  |  | Water Injection |  |  |  | 250
8300-04 |  |  |  | 43 | 59 |  |  | 8300 | 4 | 8300-04 | CC12 | CT | Cos Cob |  | 542 | 12 |  | 2008 | CAIROS | 6 | 5 | 115 |  | 1.2 | 1 | 1595 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Other Oil |  |  | Water Injection (Began Jul 01, 2008) |  |  |  | 250
8300-05 | NRG | CC13 |  | 44 | 64 | 16 |  | 8300 | 5 | 8300-05 | CC13 | CT | Cos Cob |  | 542 | 13 |  | 2010 | CAIROS | 35 | 5 | 476 |  | 1.2 | 6.5 | 10832 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Other Oil |  |  | Water Injection |  |  |  | 308
8300-05 |  |  |  | 45 | 63 |  |  | 8300 | 5 | 8300-05 | CC13 | CT | Cos Cob |  | 542 | 13 |  | 2009 | CAIROS | 8 | 5 | 155 |  | 1.2 | 1.6 | 2602 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Other Oil |  |  | Water Injection |  |  |  | 308
8300-05 |  |  |  | 46 | 62 |  |  | 8300 | 5 | 8300-05 | CC13 | CT | Cos Cob |  | 542 | 13 |  | 2008 | CAIROS | 4 | 5 | 93 |  | 1.2 | 0.8 | 1368 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) (Started May 05, 2008) | [5 empty] | Operating (Started 06/16/2008) | Combustion turbine (Started Jun 01, 2008) | Other Oil |  |  | Water Injection (Began Jun 16, 2008) |  |  |  | 308
8300-06 | NRG | CC14 |  | 47 | 67 | 17 |  | 8300 | 6 | 8300-06 | CC14 | CT | Cos Cob |  | 542 | 14 |  | 2010 | CAIROS | 42 | 5 | 604 |  | 1.2 | 7.8 | 12967 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Other Oil |  |  | Water Injection |  |  |  | 308
8300-06 |  |  |  | 48 | 66 |  |  | 8300 | 6 | 8300-06 | CC14 | CT | Cos Cob |  | 542 | 14 |  | 2009 | CAIROS | 13 | 5 | 209 |  | 1.2 | 2.5 | 4118 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Other Oil |  |  | Water Injection |  |  |  | 308
8300-06 |  |  |  | 49 | 65 |  |  | 8300 | 6 | 8300-06 | CC14 | CT | Cos Cob |  | 542 | 14 |  | 2008 | CAIROS | 4 | 5 | 91 |  | 1.2 | 0.8 | 1334 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) (Started May 05, 2008) | [5 empty] | Operating (Started 06/19/2008) | Combustion turbine (Started Jun 01, 2008) | Other Oil |  |  | Water Injection (Began Jun 19, 2008) |  |  |  | 308
8300-11 | NRG | DV10 |  | 50 | 70 | 18 |  | 8300 | 11 | 8300-11 | DV10 | CT | Devon |  | 544 | 10 |  | 2010 | CAIROS | 24 | 5 | 454 |  | 1.2 | 3.3 | 5575 | EGU | Electric Utility | 4911 | Electric Services | Devon Power, LLC (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Other Oil | [6 empty] | 230
8300-11 |  |  |  | 51 | 69 |  |  | 8300 | 11 | 8300-11 | DV10 | CT | Devon |  | 544 | 10 |  | 2009 | CAIROS | 4 | 5 | 65 |  | 1.2 | 0.5 | 869 | EGU | Electric Utility | 4911 | Electric Services | Devon Power, LLC (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Other Oil | [6 empty] | 230
8300-11 |  |  |  | 52 | 68 |  |  | 8300 | 11 | 8300-11 | DV10 | CT | Devon |  | 544 | 10 |  | 2008 | CAIROS | 6 | 5 | 112 |  | 1.2 | 0.8 | 1352 | EGU | Electric Utility | 4911 | Electric Services | Devon Power, LLC (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Other Oil | [6 empty] | 230
8300-12 | NRG | DV11 |  | 53 | 73 | 19 |  | 8300 | 12 | 8300-12 | DV11 | CT | Devon |  | 544 | 11 |  | 2010 | CAIROS | 82 | 5 | 2522 |  | 0.14 | 1.9 | 26237 | EGU | Electric Utility | 4911 | Electric Services | Devon Power, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combustion turbine | Pipeline Natural Gas | Other Oil |  | Water Injection |  |  |  | 415
8300-12 |  |  |  | 54 | 72 |  |  | 8300 | 12 | 8300-12 | DV11 | CT | Devon |  | 544 | 11 |  | 2009 | CAIROS | 18 | 5 | 496 |  | 0.15 | 0.4 | 5266 | EGU | Electric Utility | 4911 | Electric Services | Devon Power, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combustion turbine | Pipeline Natural Gas | Other Oil |  | Water Injection |  |  |  | 415
8300-12 |  |  |  | 55 | 71 |  |  | 8300 | 12 | 8300-12 | DV11 | CT | Devon |  | 544 | 11 |  | 2008 | CAIROS | 16 | 5 | 502 |  | 0.16 | 0.4 | 5219 | EGU | Electric Utility | 4911 | Electric Services | Devon Power, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combustion turbine | Pipeline Natural Gas | Other Oil |  | Water Injection |  |  |  | 400
8300-13 | NRG | DV12 |  | 56 | 76 | 20 |  | 8300 | 13 | 8300-13 | DV12 | CT | Devon |  | 544 | 12 |  | 2010 | CAIROS | 57 | 5 | 1771 |  | 0.13 | 1.2 | 18265 | EGU | Electric Utility | 4911 | Electric Services | Devon Power, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combustion turbine | Pipeline Natural Gas | Other Oil |  | Water Injection |  |  |  | 415
8300-13 |  |  |  | 57 | 75 |  |  | 8300 | 13 | 8300-13 | DV12 | CT | Devon |  | 544 | 12 |  | 2009 | CAIROS | 13 | 5 | 359 |  | 0.12 | 0.3 | 4096 | EGU | Electric Utility | 4911 | Electric Services | Devon Power, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combustion turbine | Pipeline Natural Gas | Other Oil |  | Water Injection |  |  |  | 415
8300-13 |  |  |  | 58 | 74 |  |  | 8300 | 13 | 8300-13 | DV12 | CT | Devon |  | 544 | 12 |  | 2008 | CAIROS | 16 | 5 | 470 |  | 0.13 | 0.4 | 5499 | EGU | Electric Utility | 4911 | Electric Services | Devon Power, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combustion turbine | Pipeline Natural Gas | Other Oil |  | Water Injection |  |  |  | 400
8300-14 | NRG | DV13 |  | 59 | 79 | 21 |  | 8300 | 14 | 8300-14 | DV13 | CT | Devon |  | 544 | 13 |  | 2010 | CAIROS | 85 | 5 | 2654 |  | 0.15 | 2.2 | 27875 | EGU | Electric Utility | 4911 | Electric Services | Devon Power, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combustion turbine | Pipeline Natural Gas | Other Oil |  | Water Injection |  |  |  | 415
8300-14 |  |  |  | 60 | 78 |  |  | 8300 | 14 | 8300-14 | DV13 | CT | Devon |  | 544 | 13 |  | 2009 | CAIROS | 19 | 5 | 562 |  | 0.15 | 0.5 | 5896 | EGU | Electric Utility | 4911 | Electric Services | Devon Power, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combustion turbine | Pipeline Natural Gas | Other Oil |  | Water Injection |  |  |  | 415
8300-14 |  |  |  | 61 | 77 |  |  | 8300 | 14 | 8300-14 | DV13 | CT | Devon |  | 544 | 13 |  | 2008 | CAIROS | 17 | 5 | 496 |  | 0.16 | 0.4 | 5267 | EGU | Electric Utility | 4911 | Electric Services | Devon Power, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combustion turbine | Pipeline Natural Gas | Other Oil |  | Water Injection |  |  |  | 400
8300-15 | NRG | DV14 |  | 62 | 82 | 22 |  | 8300 | 15 | 8300-15 | DV14 | CT | Devon |  | 544 | 14 |  | 2010 | CAIROS | 96 | 5 | 2945 |  | 0.15 | 2.3 | 30042 | EGU | Electric Utility | 4911 | Electric Services | Devon Power, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combustion turbine | Pipeline Natural Gas | Other Oil |  | Water Injection |  |  |  | 415
8300-15 |  |  |  | 63 | 81 |  |  | 8300 | 15 | 8300-15 | DV14 | CT | Devon |  | 544 | 14 |  | 2009 | CAIROS | 16 | 5 | 443 |  | 0.15 | 0.4 | 4653 | EGU | Electric Utility | 4911 | Electric Services | Devon Power, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combustion turbine | Pipeline Natural Gas | Other Oil |  | Water Injection |  |  |  | 415
8300-15 |  |  |  | 64 | 80 |  |  | 8300 | 15 | 8300-15 | DV14 | CT | Devon |  | 544 | 14 |  | 2008 | CAIROS | 20 | 5 | 564 |  | 0.16 | 0.5 | 5831 | EGU | Electric Utility | 4911 | Electric Services | Devon Power, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combustion turbine | Pipeline Natural Gas | Other Oil |  | Water Injection |  |  |  | 400
|  |  |  | 65 | 83 | 23 | NA |  |  |  |  | CT | Devon |  | 544 | 15 |  | 2010 | CAIROS | 7 | 3 | 286 |  | 0.02 | 0 | 2707 | EGU | Electric Utility | 4911 | Electric Services | GenConn Devon LLC (Owner / Devon Power, LLC (Operator) |  |  |  | Phase 2 |  | Operating (Started 07/10/2010) | Combustion turbine (Started Jul 10, 2010) | Other Oil | Pipeline Natural Gas |  | Water Injectio | Selective Catalytic Reduction |  |  | 474.9
|  |  |  | 66 | 85 | 24 | NA |  |  |  |  | CT | Devon |  | 544 | 16 |  | 2010 | CAIROS | 5 | 3 | 203 |  | 0.02 | 0 | 1920 | EGU | Electric Utility | 4911 | Electric Services | GenConn Devon LLC (Owner / Devon Power, LLC (Operator) |  |  |  | Phase 2 |  | Operating (Started 06/25/2010) | Combustion turbine (Started Jun 25, 2010) | Other Oil | Pipeline Natural Gas |  | Water Injection | Selective Catalytic Reduction |  |  | 589
|  |  |  | 67 | 87 | 25 | NA |  |  |  |  | CT | Devon |  | 544 | 17 |  | 2010 | CAIROS | 7 | 3 | 300 |  | 0.01 | 0 | 2769 | EGU | Electric Utility | 4911 | Electric Services | GenConn Devon LLC (Owner / Devon Power, LLC (Operator) |  |  |  | Phase 2 |  | Operating (Started 06/10/2010) | Combustion turbine (Started Jun 10, 2010) | Other Oil | Pipeline Natural Gas |  | Water Injection | Selective Catalytic Reduction |  |  | 590.6
|  |  |  | 68 | 89 | 26 | NA |  |  |  |  | CT | Devon |  | 544 | 18 |  | 2010 | CAIROS | 7 | 3 | 292 |  | 0.02 | 0 | 2803 | EGU | Electric Utility | 4911 | Electric Services | GenConn Devon LLC (Owner / Devon Power, LLC (Operator) |  |  |  | Phase 2 |  | Operating (Started 06/01/2010) | Combustion turbine (Started Jun 01, 2010) | Other Oil | Pipeline Natural Gas |  | Water Injection | Selective Catalytic Reduction |  |  | 590
#N/A |  |  |  | 69 | 93 | 27 |  | #N/A |  | #N/A | #N/A | CT | Exeter Energy Limited Partnership |  | 50736 | B1 | CS1 | 2010 | CAIROS | 3190 | 5 |  | 401260 | 0.12 | 39.8 | 679481 | EGU | Electric Utility |  |  | Exeter Energy Limited Partnership (Owner/Operator) | [5 empty] | Operating | Stoker | Tire Derived Fuel | Liquified Petroleum Gas | [5 empty] | 181
#N/A |  |  |  | 70 | 92 |  |  | #N/A |  | #N/A | #N/A | CT | Exeter Energy Limited Partnership |  | 50736 | B1 | CS1 | 2009 | CAIROS | 2885 | 5 |  | 324373 | 0.1 | 21.2 | 440239 | EGU | Electric Utility |  |  | Exeter Energy Limited Partnership (Owner/Operator) | [5 empty] | Operating | Stoker | Tire Derived Fuel | Liquified Petroleum Gas | [5 empty] | 181
#N/A |  |  |  | 71 | 91 |  |  | #N/A |  | #N/A | #N/A | CT | Exeter Energy Limited Partnership |  | 50736 | B1 | CS1 | 2008 | CAIROS | 2842 | 5 |  | 324972 | 0.11 | 48 | 913123 | EGU | Electric Utility |  |  | Exeter Energy Limited Partnership (Owner/Operator) (Started Feb 19, 2008) | [5 empty] | Operating | Stoker | Tire Derived Fuel | Liquified Petroleum Gas | [5 empty] | 181
#N/A |  |  |  | 72 | 96 | 28 |  | #N/A |  | #N/A | #N/A | CT | Exeter Energy Limited Partnership |  | 50736 | B2 | CS1 | 2010 | CAIROS | 3494 | 5 |  | 436752 | 0.12 | 43.5 | 744972 | EGU | Electric Utility |  |  | Exeter Energy Limited Partnership (Owner/Operator) | [5 empty] | Operating | Stoker | Tire Derived Fuel | Liquified Petroleum Gas | [5 empty] | 181
#N/A |  |  |  | 73 | 95 |  |  | #N/A |  | #N/A | #N/A | CT | Exeter Energy Limited Partnership |  | 50736 | B2 | CS1 | 2009 | CAIROS | 2936 | 5 |  | 326730 | 0.11 | 21.4 | 446393 | EGU | Electric Utility |  |  | Exeter Energy Limited Partnership (Owner/Operator) | [5 empty] | Operating | Stoker | Tire Derived Fuel | Liquified Petroleum Gas | [5 empty] | 181
#N/A |  |  |  | 74 | 94 |  |  | #N/A |  | #N/A | #N/A | CT | Exeter Energy Limited Partnership |  | 50736 | B2 | CS1 | 2008 | CAIROS | 2908 | 5 |  | 336464 | 0.11 | 61.4 | 1167796 | EGU | Electric Utility |  |  | Exeter Energy Limited Partnership (Owner/Operator) (Started Feb 19, 2008) | [5 empty] | Operating | Stoker | Tire Derived Fuel | Liquified Petroleum Gas | [5 empty] | 181
8300-07 | NRG | FD10 |  | 75 | 99 | 29 |  | 8300 | 7 | 8300-07 | FD10 | CT | Franklin Drive |  | 561 | 10 |  | 2010 | CAIROS | 46 | 5 | 639 |  | 1.2 | 6.9 | 11515 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Other Oil | [6 empty] | 250
8300-07 |  |  |  | 76 | 98 |  |  | 8300 | 7 | 8300-07 | FD10 | CT | Franklin Drive |  | 561 | 10 |  | 2009 | CAIROS | 5 | 5 | 62 |  | 1.2 | 0.7 | 1145 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Other Oil | [6 empty] | 250
8300-07 |  |  |  | 77 | 97 |  |  | 8300 | 7 | 8300-07 | FD10 | CT | Franklin Drive |  | 561 | 10 |  | 2008 | CAIROS | 8 | 5 | 142 |  | 1.2 | 1.2 | 2060 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Other Oil | [6 empty] | 250
#N/A |  |  |  | 78 | 102 | 30 |  | #N/A |  | #N/A | #N/A | CT | Fusion Paperboard Connecticut LLC |  | 54657 | 1 |  | 2010 | CAIROS | 3563 | 5 |  | 505847 | 0.21 | 76.2 | 706165 | NON EGU | Pulp & Paper Mill | 2653 | Corrugated and Solid Fiber Box | Fusion Paperboard Connecticut LLC (Owner/Operator) | [5 empty] | Operating | Dry bottom wall-fired boiler | Pipeline Natural Gas | Residual Oil |  | Low NOx Burner Technology (Dry Bottom only) |  |  |  | 275
#N/A |  |  |  | 79 | 101 |  |  | #N/A |  | #N/A | #N/A | CT | Fusion Paperboard Connecticut LLC |  | 54657 | 1 |  | 2009 | CAIROS | 3290 | 5 |  | 460096 | 0.22 | 72.8 | 639126 | NON EGU | Pulp & Paper Mill | 2653 | Corrugated and Solid Fiber Box | Fusion Paperboard Connecticut LLC (Owner/Operator) | [5 empty] | Operating | Dry bottom wall-fired boiler | Pipeline Natural Gas | Residual Oil |  | Low NOx Burner Technology (Dry Bottom only) |  |  |  | 275
#N/A |  |  |  | 80 | 100 |  |  | #N/A |  | #N/A | #N/A | CT | Fusion Paperboard Connecticut LLC |  | 54657 | 1 |  | 2008 | CAIROS | 3346 | 5 |  | 381076 | 0.14 | 40 | 519447 | NON EGU | Pulp & Paper Mill | 2653 | Corrugated and Solid Fiber Box | Fusion Paperboard Connecticut LLC (Owner/Operator) | [5 empty] | Operating | Dry bottom wall-fired boiler | Pipeline Natural Gas | Residual Oil |  | Low NOx Burner Technology (Dry Bottom only) |  |  |  | 275
#N/A |  |  |  | 81 | 109 | 31 |  | #N/A |  | #N/A | #N/A | CT | Lake Road Generating Company |  | 55149 | LRG1 |  | 2010 | CAIROS | 2875 | 5 | 441982 |  | 0.01 | 16.5 | 4779615 | EGU | Electric Utility | 4911 | Electric Services | Lake Road Generating Company, LP (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combined cycle | Pipeline Natural Gas | Diesel Oil |  | Dry Low NOx Burner | Water Injection | Selective Catalytic Reduction |  | 2276
#N/A |  |  |  | 82 | 106 |  |  | #N/A |  | #N/A | #N/A | CT | Lake Road Generating Company |  | 55149 | LRG1 |  | 2009 | CAIROS | 2194 | 5 | 327804 |  | 0.01 | 12.5 | 3571803 | EGU | Electric Utility | 4911 | Electric Services | Lake Road Generating Company, LP (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combined cycle | Pipeline Natural Gas | Diesel Oil |  | Dry Low NOx Burner | Water Injection | Selective Catalytic Reduction |  | 2276
#N/A |  |  |  | 83 | 103 |  |  | #N/A |  | #N/A | #N/A | CT | Lake Road Generating Company |  | 55149 | LRG1 |  | 2008 | CAIROS | 1438 | 5 | 209512 |  | 0.01 | 8.8 | 2313832 | EGU | Electric Utility | 4911 | Electric Services | Lake Road Generating Company, LP (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combined cycle | Pipeline Natural Gas | Diesel Oil |  | Dry Low NOx Burner | Water Injection | Selective Catalytic Reduction |  | 2276
#N/A |  |  |  | 84 | 118 | 32 |  | #N/A |  | #N/A | #N/A | CT | Lake Road Generating Company |  | 55149 | LRG2 |  | 2010 | CAIROS | 2543 | 5 | 391535 |  | 0.01 | 15 | 4170699 | EGU | Electric Utility | 4911 | Electric Services | Lake Road Generating Company, LP (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combined cycle | Pipeline Natural Gas | Diesel Oil |  | Dry Low NOx Burner | Water Injection | Selective Catalytic Reduction |  | 2276
#N/A |  |  |  | 85 | 115 |  |  | #N/A |  | #N/A | #N/A | CT | Lake Road Generating Company |  | 55149 | LRG2 |  | 2009 | CAIROS | 1845 | 5 | 278005 |  | 0.01 | 10.2 | 2975713 | EGU | Electric Utility | 4911 | Electric Services | Lake Road Generating Company, LP (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combined cycle | Pipeline Natural Gas | Diesel Oil |  | Dry Low NOx Burner | Water Injection | Selective Catalytic Reduction |  | 2276
#N/A |  |  |  | 86 | 112 |  |  | #N/A |  | #N/A | #N/A | CT | Lake Road Generating Company |  | 55149 | LRG2 |  | 2008 | CAIROS | 1692 | 5 | 254939 |  | 0.02 | 13.4 | 2764477 | EGU | Electric Utility | 4911 | Electric Services | Lake Road Generating Company, LP (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combined cycle | Pipeline Natural Gas | Diesel Oil |  | Dry Low NOx Burner | Water Injection | Selective Catalytic Reduction |  | 2276
#N/A |  |  |  | 87 | 127 | 33 |  | #N/A |  | #N/A | #N/A | CT | Lake Road Generating Company |  | 55149 | LRG3 |  | 2010 | CAIROS | 2682 | 5 | 421801 |  | 0.01 | 12.6 | 4582273 | EGU | Electric Utility | 4911 | Electric Services | Lake Road Generating Company, LP (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combined cycle | Pipeline Natural Gas | Diesel Oil |  | Dry Low NOx Burner | Water Injection | Selective Catalytic Reduction |  | 2276
#N/A |  |  |  | 88 | 124 |  |  | #N/A |  | #N/A | #N/A | CT | Lake Road Generating Company |  | 55149 | LRG3 |  | 2009 | CAIROS | 1563 | 5 | 228387 |  | 0.01 | 9.2 | 2544572 | EGU | Electric Utility | 4911 | Electric Services | Lake Road Generating Company, LP (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combined cycle | Pipeline Natural Gas | Diesel Oil |  | Dry Low NOx Burner | Water Injection | Selective Catalytic Reduction |  | 2276
#N/A |  |  |  | 89 | 121 |  |  | #N/A |  | #N/A | #N/A | CT | Lake Road Generating Company |  | 55149 | LRG3 |  | 2008 | CAIROS | 1922 | 5 | 288143 |  | 0.02 | 14 | 3289277 | EGU | Electric Utility | 4911 | Electric Services | Lake Road Generating Company, LP (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combined cycle | Pipeline Natural Gas | Diesel Oil |  | Dry Low NOx Burner | Water Injection | Selective Catalytic Reduction |  | 2276
8300-09 | NRG | MD10 |  | 90 | 136 | 34 |  | 8300 | 9 | 8300-09 | MD10 | CT | Middletown |  | 562 | 10 |  | 2010 | CAIROS | 95 | 5 | 1275 |  | 1.2 | 14.3 | 23750 | EGU | Electric Utility | 4911 | Electric Services | Middletown Power, LLC (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Other Oil | [6 empty] | 250
8300-09 |  |  |  | 91 | 132 |  |  | 8300 | 9 | 8300-09 | MD10 | CT | Middletown |  | 562 | 10 |  | 2009 | CAIROS | 20 | 5 | 243 |  | 1.2 | 3 | 5013 | EGU | Electric Utility | 4911 | Electric Services | Middletown Power, LLC (Owner/Operator) (Started Apr 08, 2009) | [5 empty] | Operating | Combustion turbine | Other Oil | [6 empty] | 250
8300-09 |  |  |  | 92 | 130 |  |  | 8300 | 9 | 8300-09 | MD10 | CT | Middletown |  | 562 | 10 |  | 2008 | CAIROS | 17 | 5 | 405 |  | 1.2 | 2.6 | 4250 | EGU | Electric Utility | 4911 | Electric Services | Middletown Power, LLC (Owner) / NRG Energy, Inc (Operator) | [5 empty] | Operating | Combustion turbine | Other Oil | [6 empty] | 250
8306-01 | NRG | MD2 |  | 93 | 142 | 35 | 6 | 8306 | 1 | 8306-01 | MD2 | CT | Middletown |  | 562 | 2 |  | 2010 | CAIROS | 1670 | 5 | 111835 |  | 0.12 | 94.2 | 1434563 | EGU | Electric Utility | 4911 | Electric Services | Middletown Power, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Dry bottom wall-fired boiler | Residual Oil | Pipeline Natural Gas |  | Overfire Air |  |  | Electrostatic Precipitator | 1295
8306-01 |  |  |  | 94 | 139 |  | 6 | 8306 | 1 | 8306-01 | MD2 | CT | Middletown |  | 562 | 2 |  | 2009 | CAIROS | 647 | 5 | 40226 |  | 0.12 | 38.5 | 528197 | EGU | Electric Utility | 4911 | Electric Services | Middletown Power, LLC (Owner/Operator) (Started Apr 07, 2009) |  |  |  | Phase 2 |  | Operating | Dry bottom wall-fired boiler | Residual Oil | Pipeline Natural Gas |  | Overfire Air |  |  | Electrostatic Precipitator | 1295
8306-01 |  |  |  | 95 | 137 |  | 6 | 8306 | 1 | 8306-01 | MD2 | CT | Middletown |  | 562 | 2 |  | 2008 | CAIROS | 501 | 5 | 32545 |  | 0.12 | 33.5 | 467707 | EGU | Electric Utility | 4911 | Electric Services | Middletown Power, LLC (Owner) / NRG Energy, Inc (Operator) |  |  |  | Phase 2 |  | Operating | Dry bottom wall-fired boiler | Residual Oil | Pipeline Natural Gas |  | Overfire Air |  |  | Electrostatic Precipitator | 1295
8306-02 | NRG | MD3 |  | 96 | 148 | 36 | 6 | 8306 | 2 | 8306-02 | MD3 | CT | Middletown |  | 562 | 3 |  | 2010 | CAIROS | 1084 | 5 | 141127 |  | 0.18 | 189.3 | 1790536 | EGU | Electric Utility | 4911 | Electric Services | Middletown Power, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Cyclone boiler | Residual Oil | Pipeline Natural Gas |  | Water Injection | Selective Non-catalytic Reduction |  | Electrostatic Precipitator | 2370
8306-02 |  |  |  | 97 | 145 |  | 6 | 8306 | 2 | 8306-02 | MD3 | CT | Middletown |  | 562 | 3 |  | 2009 | CAIROS | 293 | 5 | 41047 |  | 0.23 | 54.4 | 445004 | EGU | Electric Utility | 4911 | Electric Services | Middletown Power, LLC (Owner/Operator) (Started Apr 08, 2009) |  |  |  | Phase 2 |  | Operating | Cyclone boiler | Residual Oil | Pipeline Natural Gas |  | Water Injection | Selective Non-catalytic Reduction |  | Electrostatic Precipitator | 2370
8306-02 |  |  |  | 98 | 143 |  | 6 | 8306 | 2 | 8306-02 | MD3 | CT | Middletown |  | 562 | 3 |  | 2008 | CAIROS | 315 | 5 | 32767 |  | 0.28 | 83.7 | 495983 | EGU | Electric Utility | 4911 | Electric Services | Middletown Power, LLC (Owner) / NRG Energy, Inc (Operator) |  |  |  | Phase 2 |  | Operating | Cyclone boiler | Residual Oil | Pipeline Natural Gas |  | Water Injection | Selective Non-catalytic Reduction |  | Electrostatic Precipitator | 2370
8306-03 | NRG | MD4 |  | 99 | 154 | 37 | 6 | 8306 | 3 | 8306-03 | MD4 | CT | Middletown |  | 562 | 4 |  | 2010 | CAIROS | 461 | 5 | 55670 |  | 0.16 | 80.5 | 880454 | EGU | Electric Utility | 4911 | Electric Services | Middletown Power, LLC (Owner) / NRG Energy, Inc (Operator |  |  |  | Phase 2 |  | Operating | Tangentially-fired | Residual Oil | [6 empty] | 4684
8306-03 |  |  |  | 100 | 152 |  | 6 | 8306 | 3 | 8306-03 | MD4 | CT | Middletown |  | 562 | 4 |  | 2009 | CAIROS | 74 | 5 | 10926 |  | 0.16 | 16.8 | 173766 | EGU | Electric Utility | 4911 | Electric Services | Middletown Power, LLC (Owner) / NRG Energy, Inc (Operator |  |  |  | Phase 2 |  | Operating | Tangentially-fired | Residual Oil | [6 empty] | 4684
8306-03 |  |  |  | 101 | 150 |  | 6 | 8306 | 3 | 8306-03 | MD4 | CT | Middletown |  | 562 | 4 |  | 2008 | CAIROS | 131 | 5 | 15578 |  | 0.16 | 21 | 224548 | EGU | Electric Utility | 4911 | Electric Services | Middletown Power, LLC (Owner) / NRG Energy, Inc (Operator |  |  |  | Phase 2 |  | Operating | Tangentially-fired | Residual Oil | [6 empty] | 4684
#N/A |  |  |  | 102 | 160 | 38 |  | #N/A |  | #N/A | #N/A | CT | Milford Power Company LLC |  | 55126 | CT01 |  | 2010 | CAIROS | 3519 | 5 | 877801 |  | 0.01 | 18 | 6021300 | EGU | Electric Utility |  |  | Milford Power Company, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combined cycle | Pipeline Natural Gas | Diesel Oil |  | Water Injection | Selective Catalytic Reduction |  |  | 2064
#N/A |  |  |  | 103 | 158 |  |  | #N/A |  | #N/A | #N/A | CT | Milford Power Company LLC |  | 55126 | CT01 |  | 2009 | CAIROS | 3120 | 5 | 725722 |  | 0.01 | 18.3 | 4909716 | EGU | Electric Utility |  |  | Milford Power Company, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combined cycle | Pipeline Natural Gas | Diesel Oil |  | Water Injection | Selective Catalytic Reduction |  |  | 2064
#N/A |  |  |  | 104 | 156 |  |  | #N/A |  | #N/A | #N/A | CT | Milford Power Company LLC |  | 55126 | CT01 |  | 2008 | CAIROS | 2734 | 5 | 612534 |  | 0.02 | 16.4 | 4214594 | EGU | Electric Utility |  |  | Milford Power Company, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combined cycle | Pipeline Natural Gas | Diesel Oil |  | Water Injection | Selective Catalytic Reduction |  |  | 2064
#N/A |  |  |  | 105 | 166 | 39 |  | #N/A |  | #N/A | #N/A | CT | Milford Power Company LLC |  | 55126 | CT02 |  | 2010 | CAIROS | 2824 | 5 | 702885 |  | 0.01 | 16.6 | 4990590 | EGU | Electric Utility |  |  | Milford Power Company, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combined cycle | Pipeline Natural Gas | Diesel Oil |  | Water Injection | Selective Catalytic Reduction |  |  | 2082
#N/A |  |  |  | 106 | 164 |  |  | #N/A |  | #N/A | #N/A | CT | Milford Power Company LLC |  | 55126 | CT02 |  | 2009 | CAIROS | 3162 | 5 | 742505 |  | 0.02 | 19.9 | 5169995 | EGU | Electric Utility |  |  | Milford Power Company, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combined cycle | Pipeline Natural Gas | Diesel Oil |  | Water Injection | Selective Catalytic Reduction |  |  | 2064
#N/A |  |  |  | 107 | 162 |  |  | #N/A |  | #N/A | #N/A | CT | Milford Power Company LLC |  | 55126 | CT02 |  | 2008 | CAIROS | 2710 | 5 | 618784 |  | 0.01 | 16.5 | 4375717 | EGU | Electric Utility |  |  | Milford Power Company, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combined cycle | Pipeline Natural Gas | Diesel Oil |  | Water Injection | Selective Catalytic Reduction |  |  | 2064
8306-04 | NRG | MV5 |  | 108 | 170 | 40 | 6 | 8306 | 4 | 8306-04 | MV5 | CT | Montville |  | 546 | 5 |  | 2010 | CAIROS | 932 | 5 | 45896 |  | 0.09 | 27.4 | 567960 | EGU | Electric Utility | 4911 | Electric Services | Montville Power, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Tangentially-fired | Residual Oil | Pipeline Natural Gas |  |  |  |  | Electrostatic Precipitator | 995
8300-0 |  |  |  | 109 | 169 |  |  | 8300 |  | 8300-0 | #N/A | CT | Montville |  | 546 | 5 |  | 2009 | CAIROS | 112 | 5 | 6227 |  | 0.1 | 4.6 | 75780 | EGU | Electric Utility | 4911 | Electric Services | Montville Power, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Tangentially-fired | Residual Oil | Pipeline Natural Gas |  |  |  |  | Electrostatic Precipitator | 995
8300-0 |  |  |  | 110 | 168 |  |  | 8300 |  | 8300-0 | #N/A | CT | Montville |  | 546 | 5 |  | 2008 | CAIROS | 245 | 5 | 12536 |  | 0.09 | 8 | 148000 | EGU | Electric Utility | 4911 | Electric Services | Montville Power, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Tangentially-fired | Residual Oil | Pipeline Natural Gas |  |  |  |  | Electrostatic Precipitator | 995
8306-05 | NRG | MV6 |  | 111 | 173 | 41 | 6 | 8306 | 5 | 8306-05 | MV6 | CT | Montville |  | 546 | 6 |  | 2010 | CAIROS | 376 | 5 | 41495 |  | 0.14 | 44.3 | 608716 | EGU | Electric Utility | 4911 | Electric Services | Montville Power, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Tangentially-fired | Residual Oil | [6 empty] | 4658
8300-0 |  |  |  | 112 | 172 |  |  | 8300 |  | 8300-0 | #N/A | CT | Montville |  | 546 | 6 |  | 2009 | CAIROS | 146 | 5 | 16484 |  | 0.16 | 25.4 | 253965 | EGU | Electric Utility | 4911 | Electric Services | Montville Power, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Tangentially-fired | Residual Oil | [6 empty] | 4658
8300-0 |  |  |  | 113 | 171 |  |  | 8300 |  | 8300-0 | #N/A | CT | Montville |  | 546 | 6 |  | 2008 | CAIROS | 79 | 5 | 14294 |  | 0.16 | 17.3 | 178548 | EGU | Electric Utility | 4911 | Electric Services | Montville Power, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Tangentially-fired | Residual Oil | [6 empty] | 4658
8305-01 | PSEG | NHB1 |  | 114 | 176 | 42 |  | 8305 | 1 | 8305-01 | NHB1 | CT | New Haven Harbor |  | 6156 | NHB1 |  | 2010 | CAIROS | 849 | 5 | 136402 |  | 0.13 | 102 | 1485780 | EGU | Electric Utility | 4911 | Electric Services | PSEG (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Tangentially-fired | Residual Oil | Diesel Oil, Pipeline Natural Gas |  |  |  |  | Electrostatic Precipitator | 4286
8305-01 |  |  |  | 115 | 175 |  |  | 8305 | 1 | 8305-01 | NHB1 | CT | New Haven Harbor |  | 6156 | NHB1 |  | 2009 | CAIROS | 205 | 5 | 26780 |  | 0.14 | 23.9 | 306139 | EGU | Electric Utility | 4911 | Electric Services | PSEG (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Tangentially-fired | Residual Oil | Diesel Oil, Pipeline Natural Gas |  |  |  |  | Electrostatic Precipitator | 4286
8305-01 |  |  |  | 116 | 174 |  |  | 8305 | 1 | 8305-01 | NHB1 | CT | New Haven Harbor |  | 6156 | NHB1 |  | 2008 | CAIROS | 227 | 5 | 35856 |  | 0.15 | 32.2 | 390698 | EGU | Electric Utility | 4911 | Electric Services | PSEG (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Tangentially-fired | Residual Oil | Diesel Oil, Pipeline Natural Gas |  |  |  |  | Electrostatic Precipitator | 4286
8306-06 | NRG | NH1 |  | 117 | 179 | 43 | 6 | 8306 | 6 | 8306-06 | NH1 | CT | Norwalk Harbor Station |  | 548 | 1 | CS0001 | 2010 | CAIROS | 707 | 5 | 32380 |  | 0.13 | 30.6 | 374772 | EGU | Electric Utility | 4911 | Electric Services | Norwalk Power, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Tangentially-fired | Residual Oil |  |  | Selective Non-catalytic Reduction |  |  | Electrostatic Precipitator | 1776
8300-06 |  |  |  | 118 | 178 |  |  | 8300 | 6 | 8300-06 | CC14 | CT | Norwalk Harbor Station |  | 548 | 1 | CS0001 | 2009 | CAIROS | 219 | 5 | 8286 |  | 0.1 | 7.6 | 101788 | EGU | Electric Utility | 4911 | Electric Services | Norwalk Power, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Tangentially-fired | Residual Oil |  |  | Selective Non-catalytic Reduction |  |  | Electrostatic Precipitator | 1776
8300-06 |  |  |  | 119 | 177 |  |  | 8300 | 6 | 8300-06 | CC14 | CT | Norwalk Harbor Station |  | 548 | 1 | CS0001 | 2008 | CAIROS | 829 | 5 | 48368 |  | 0.14 | 49.5 | 624903 | EGU | Electric Utility | 4911 | Electric Services | Norwalk Power, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Tangentially-fired | Residual Oil |  |  | Selective Non-catalytic Reduction |  |  | Electrostatic Precipitator | 1776
8300-10 | NRG | NH10 |  | 120 | 182 | 44 |  | 8300 | 10 | 8300-10 | NH10 | CT | Norwalk Harbor Station |  | 548 | 10 |  | 2010 | CAIROS | 21 | 5 | 204 |  | 1.17 | 0 | 13 | EGU | Electric Utility | 4911 | Electric Services | Norwalk Power, LLC (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Other Oil | [6 empty] | 232
8300-0 |  |  |  | 121 | 181 |  |  | 8300 |  | 8300-0 | #N/A | CT | Norwalk Harbor Station |  | 548 | 10 |  | 2009 | CAIROS | 6 | 5 | 55 |  | 1.17 | 0 | 4 | EGU | Electric Utility | 4911 | Electric Services | Norwalk Power, LLC (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Other Oil | [6 empty] | 232
8300-0 |  |  |  | 122 | 180 |  |  | 8300 |  | 8300-0 | #N/A | CT | Norwalk Harbor Station |  | 548 | 10 |  | 2008 | CAIROS | 8 | 5 | 67 |  | 1.18 | 0.3 | 468 | EGU | Electric Utility | 4911 | Electric Services | Norwalk Power, LLC (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Other Oil | [6 empty] | 232
8306-07 | NRG | NH2 |  | 123 | 185 | 45 | 6 | 8306 | 7 | 8306-07 | NH2 | CT | Norwalk Harbor Station |  | 548 | 2 | CS0001 | 2010 | CAIROS | 711 | 5 | 35972 |  | 0.13 | 34.3 | 420206 | EGU | Electric Utility | 4911 | Electric Services | Norwalk Power, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Tangentially-fired | Residual Oil |  |  | Selective Non-catalytic Reduction |  |  | Electrostatic Precipitator | 1776
8300-07 |  |  |  | 124 | 184 |  |  | 8300 | 7 | 8300-07 | FD10 | CT | Norwalk Harbor Station |  | 548 | 2 | CS0001 | 2009 | CAIROS | 184 | 5 | 10175 |  | 0.13 | 9.1 | 123688 | EGU | Electric Utility | 4911 | Electric Services | Norwalk Power, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Tangentially-fired | Residual Oil |  |  | Selective Non-catalytic Reduction |  |  | Electrostatic Precipitator | 1776
8300-07 |  |  |  | 125 | 183 |  |  | 8300 | 7 | 8300-07 | FD10 | CT | Norwalk Harbor Station |  | 548 | 2 | CS0001 | 2008 | CAIROS | 1523 | 5 | 75250 |  | 0.13 | 76.7 | 1027131 | EGU | Electric Utility | 4911 | Electric Services | Norwalk Power, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Tangentially-fired | Residual Oil |  |  | Selective Non-catalytic Reduction |  |  | Electrostatic Precipitator | 1776
8304-01 | NPU | TRBINE |  | 126 | 188 | 46 |  | 8304 | 1 | 8304-01 | TRBINE | CT | Norwich |  | 581 | TRBINE |  | 2010 | CAIROS | 19 | 5 | 327 |  | 0.62 | 1.5 | 4811 | EGU | Electric Utility | 4911 | Electric Services | Norwich Public Utilities (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Diesel Oil | [6 empty] | 249
8304-01 |  |  |  | 127 | 187 |  |  | 8304 | 1 | 8304-01 | TRBINE | CT | Norwich |  | 581 | TRBINE |  | 2009 | CAIROS | 15 | 5 | 225 |  | 0.62 | 1.2 | 3782 | EGU | Electric Utility | 4911 | Electric Services | Norwich Public Utilities (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Diesel Oil | [6 empty] | 249
8304-01 |  |  |  | 128 | 186 |  |  | 8304 | 1 | 8304-01 | TRBINE | CT | Norwich |  | 581 | TRBINE |  | 2008 | CAIROS | 10 | 5 | 151 |  | 0.57 | 0.7 | 2595 | EGU | Electric Utility | 4911 | Electric Services | Norwich Public Utilities (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Diesel Oil | [6 empty] | 249
#N/A |  |  |  | 129 | 191 | 47 |  | #N/A |  | #N/A | #N/A | CT | Pfizer |  | 54236 | 5 |  | 2010 | CAIROS | 2398 | 5 |  | 271195 | 0.12 | 20.7 | 329666 | NON EGU | Industrial Boiler | 2834 | Pharmaceutical Preparations | Pfizer, Inc. (Owner/Operator) | [5 empty] | Operating | Dry bottom wall-fired boiler | Residual Oil | Pipeline Natural Gas | [5 empty] | 501.6
#N/A |  |  |  | 130 | 190 |  |  | #N/A |  | #N/A | #N/A | CT | Pfizer |  | 54236 | 5 |  | 2009 | CAIROS | 2122 | 5 |  | 225223 | 0.16 | 21.8 | 275275 | NON EGU | Industrial Boiler | 2834 | Pharmaceutical Preparations | Pfizer, Inc. (Owner/Operator) | [5 empty] | Operating | Dry bottom wall-fired boiler | Residual Oil | Pipeline Natural Gas | [5 empty] | 501.6
#N/A |  |  |  | 131 | 189 |  |  | #N/A |  | #N/A | #N/A | CT | Pfizer |  | 54236 | 5 |  | 2008 | CAIROS | 895 | 5 |  | 93448 | 0.09 | 4.9 | 109675 | NON EGU | Industrial Boiler | 2834 | Pharmaceutical Preparations | Pfizer, Inc. (Owner/Operator) | [5 empty] | Operating | Dry bottom wall-fired boiler | Residual Oil | Pipeline Natural Gas | [5 empty] | 400
#N/A |  |  |  | 1: 132; 2: 192; 3: 48; 5: #N/A; 7: #N/A; 8: #N/A; 9: CT; 10: Pfizer; 12: 54236; 13: 8; 15: 2008; 16: CAIROS; 17: 0; 18: 5; 24: NON EGU; 25: Industrial Boiler; 26: 2834; 27: Pharmaceutical Preparations; 28: Pfizer, Inc. (Owner/Operator); 34: Operating (Retired 09/30/2008); 35: Dry bottom wall-fired boiler; 36: Residual Oil; 37: Pipeline Natural Gas; 43: 266
#N/A |  |  |  | 133 | 197 | 49 |  | #N/A |  | #N/A | #N/A | CT | Pratt & Whitney, East Hartford |  | 54605 | 001 |  | 2010 | CAIROS | 2428 | 5 | 59851 |  | 0.02 | 7.1 | 648271 | NON EGU | Cogeneration | 3511 | Turbines and Turbine Generator | P&W, Division of United Technologies (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Pipeline Natural Gas | Diesel Oil |  | Water Injection | Selective Catalytic Reduction |  |  | 365.7
#N/A |  |  |  | 134 | 195 |  |  | #N/A |  | #N/A | #N/A | CT | Pratt & Whitney, East Hartford |  | 54605 | 001 |  | 2009 | CAIROS | 2590 | 5 | 64108 |  | 0.02 | 7.8 | 694555 | NON EGU | Cogeneration | 3511 | Turbines and Turbine Generator | P&W, Division of United Technologies (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Pipeline Natural Gas | Diesel Oil |  | Water Injection | Selective Catalytic Reduction |  |  | 365.7
#N/A |  |  |  | 135 | 193 |  |  | #N/A |  | #N/A | #N/A | CT | Pratt & Whitney, East Hartford |  | 54605 | 001 |  | 2008 | CAIROS | 3198 | 5 | 75029 |  | 0.02 | 9.3 | 834875 | NON EGU | Cogeneration | 3511 | Turbines and Turbine Generator | P&W, Division of United Technologies (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Pipeline Natural Gas | Diesel Oil |  | Water Injection | Selective Catalytic Reduction |  |  | 365.7
8302-01 | CRRA | 11A |  | 136 | 201 | 50 |  | 8302 | 1 | 8302-01 | 11A | CT | South Meadow Station |  | 563 | 11A |  | 2010 | CAIROS | 15 | 5 | 221 |  | 0.75 | 1.1 | 2925 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Resources Recovery Authority (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-01 |  |  |  | 137 | 200 |  |  | 8302 | 1 | 8302-01 | 11A | CT | South Meadow Station |  | 563 | 11A |  | 2009 | CAIROS | 8 | 5 | 68 |  | 0.85 | 0.4 | 869 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Resources Recovery Authority (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-01 |  |  |  | 138 | 199 |  |  | 8302 | 1 | 8302-01 | 11A | CT | South Meadow Station |  | 563 | 11A |  | 2008 | CAIROS | 12 | 5 | 126 |  | 0.83 | 0.7 | 1575 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Resources Recovery Authority (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-02 | CRRA | 11B |  | 139 | 204 | 51 |  | 8302 | 2 | 8302-02 | 11B | CT | South Meadow Station |  | 563 | 11B |  | 2010 | CAIROS | 15 | 5 | 221 |  | 0.76 | 1.1 | 2925 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Resources Recovery Authority (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-02 |  |  |  | 140 | 203 |  |  | 8302 | 2 | 8302-02 | 11B | CT | South Meadow Station |  | 563 | 11B |  | 2009 | CAIROS | 8 | 5 | 68 |  | 0.75 | 0.3 | 869 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Resources Recovery Authority (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-02 |  |  |  | 141 | 202 |  |  | 8302 | 2 | 8302-02 | 11B | CT | South Meadow Station |  | 563 | 11B |  | 2008 | CAIROS | 12 | 5 | 126 |  | 0.73 | 0.6 | 1575 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Resources Recovery Authority (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-03 | CRRA | 12A |  | 142 | 207 | 52 |  | 8302 | 3 | 8302-03 | 12A | CT | South Meadow Station |  | 563 | 12A |  | 2010 | CAIROS | 19 | 5 | 285 |  | 0.8 | 1.5 | 3819 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Resources Recovery Authority (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-03 |  |  |  | 143 | 206 |  |  | 8302 | 3 | 8302-03 | 12A | CT | South Meadow Station |  | 563 | 12A |  | 2009 | CAIROS | 7 | 5 | 78 |  | 0.82 | 0.4 | 1013 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Resources Recovery Authority (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-03 |  |  |  | 144 | 205 |  |  | 8302 | 3 | 8302-03 | 12A | CT | South Meadow Station |  | 563 | 12A |  | 2008 | CAIROS | 11 | 5 | 123 |  | 0.8 | 0.6 | 1560 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Resources Recovery Authority (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-04 | CRRA | 12B |  | 145 | 210 | 53 |  | 8302 | 4 | 8302-04 | 12B | CT | South Meadow Station |  | 563 | 12B |  | 2010 | CAIROS | 19 | 5 | 285 |  | 0.76 | 1.5 | 3819 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Resources Recovery Authority (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-04 |  |  |  | 146 | 209 |  |  | 8302 | 4 | 8302-04 | 12B | CT | South Meadow Station |  | 563 | 12B |  | 2009 | CAIROS | 7 | 5 | 78 |  | 0.74 | 0.4 | 1013 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Resources Recovery Authority (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-04 |  |  |  | 147 | 208 |  |  | 8302 | 4 | 8302-04 | 12B | CT | South Meadow Station |  | 563 | 12B |  | 2008 | CAIROS | 11 | 5 | 123 |  | 0.72 | 0.6 | 1560 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Resources Recovery Authority (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-05 | CRRA | 13A |  | 148 | 213 | 54 |  | 8302 | 5 | 8302-05 | 13A | CT | South Meadow Station |  | 563 | 13A |  | 2010 | CAIROS | 18 | 5 | 248 |  | 0.81 | 1.4 | 3313 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Resources Recovery Authority (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-05 |  |  |  | 149 | 212 |  |  | 8302 | 5 | 8302-05 | 13A | CT | South Meadow Station |  | 563 | 13A |  | 2009 | CAIROS | 8 | 5 | 72 |  | 0.86 | 0.4 | 910 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Resources Recovery Authority (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-05 |  |  |  | 150 | 211 |  |  | 8302 | 5 | 8302-05 | 13A | CT | South Meadow Station |  | 563 | 13A |  | 2008 | CAIROS | 12 | 5 | 111 |  | 0.88 | 0.6 | 1405 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Resources Recovery Authority (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-06 | CRRA | 13B |  | 151 | 216 | 55 |  | 8302 | 6 | 8302-06 | 13B | CT | South Meadow Station |  | 563 | 13B |  | 2010 | CAIROS | 18 | 5 | 248 |  | 0.79 | 1.3 | 3313 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Resources Recovery Authority (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-06 |  |  |  | 152 | 215 |  |  | 8302 | 6 | 8302-06 | 13B | CT | South Meadow Station |  | 563 | 13B |  | 2009 | CAIROS | 8 | 5 | 72 |  | 0.82 | 0.4 | 910 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Resources Recovery Authority (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-06 |  |  |  | 153 | 214 |  |  | 8302 | 6 | 8302-06 | 13B | CT | South Meadow Station |  | 563 | 13B |  | 2008 | CAIROS | 12 | 5 | 111 |  | 0.84 | 0.6 | 1405 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Resources Recovery Authority (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-07 | CRRA | 14A |  | 154 | 219 | 56 |  | 8302 | 7 | 8302-07 | 14A | CT | South Meadow Station |  | 563 | 14A |  | 2010 | CAIROS | 16 | 5 | 220 |  | 0.82 | 1.2 | 2931 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Resources Recovery Authority (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-07 |  |  |  | 155 | 218 |  |  | 8302 | 7 | 8302-07 | 14A | CT | South Meadow Station |  | 563 | 14A |  | 2009 | CAIROS | 6 | 5 | 64 |  | 0.86 | 0.4 | 825 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Resources Recovery Authority (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-07 |  |  |  | 156 | 217 |  |  | 8302 | 7 | 8302-07 | 14A | CT | South Meadow Station |  | 563 | 14A |  | 2008 | CAIROS | 9 | 5 | 89 |  | 0.87 | 0.5 | 1135 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Resources Recovery Authority (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-08 | CRRA | 14B |  | 157 | 222 | 57 |  | 8302 | 8 | 8302-08 | 14B | CT | South Meadow Station |  | 563 | 14B |  | 2010 | CAIROS | 16 | 5 | 220 |  | 0.84 | 1.2 | 2931 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Resources Recovery Authority (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-08 |  |  |  | 158 | 221 |  |  | 8302 | 8 | 8302-08 | 14B | CT | South Meadow Station |  | 563 | 14B |  | 2009 | CAIROS | 6 | 5 | 64 |  | 0.73 | 0.3 | 825 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Resources Recovery Authority (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-08 |  |  |  | 159 | 220 |  |  | 8302 | 8 | 8302-08 | 14B | CT | South Meadow Station |  | 563 | 14B |  | 2008 | CAIROS | 9 | 5 | 89 |  | 0.74 | 0.4 | 1135 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Resources Recovery Authority (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8300-08 | NRG | TT10 |  | 160 | 225 | 58 |  | 8300 | 8 | 8300-08 | TT10 | CT | Torrington Terminal |  | 565 | 10 |  | 2010 | CAIROS | 36 | 5 | 468 |  | 1.2 | 5.4 | 9070 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Other Oil | [6 empty] | 250
8300-08 |  |  |  | 161 | 224 |  |  | 8300 | 8 | 8300-08 | TT10 | CT | Torrington Terminal |  | 565 | 10 |  | 2009 | CAIROS | 6 | 5 | 91 |  | 1.2 | 0.8 | 1408 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Other Oil | [6 empty] | 250
8300-08 |  |  |  | 162 | 223 |  |  | 8300 | 8 | 8300-08 | TT10 | CT | Torrington Terminal |  | 565 | 10 |  | 2008 | CAIROS | 6 | 5 | 111 |  | 1.2 | 0.9 | 1450 | EGU | Electric Utility | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Other Oil | [6 empty] | 250
8303-01 | FirstLight | 10 |  | 163 | 232 | 59 |  | 8303 | 1 | 8303-01 | 10 | CT | Tunnel |  | 557 | 10 |  | 2010 | CAIROS | 20 | 5 | 301 |  | 0.73 | 1.7 | 4575 | EGU | Electric Utility | 4911 | Electric Services | FirstLight Hydro Generating Company (Owner) (Started Oct 19, 2010) | [5 empty] | Operating | Combustion turbine | Diesel Oil | [6 empty] | 243
8303-01 |  |  |  | 164 | 229 |  |  | 8303 | 1 | 8303-01 | 10 | CT | Tunnel |  | 557 | 10 |  | 2009 | CAIROS | 3 | 5 | 46 |  | 0.79 | 0.3 | 808 | EGU | Electric Utility | 4911 | Electric Services | FirstLight Power Resources (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Diesel Oil | [6 empty] | 243
8303-01 |  |  |  | 165 | 226 |  |  | 8303 | 1 | 8303-01 | 10 | CT | Tunnel |  | 557 | 10 |  | 2008 | CAIROS | 15 | 5 | 153 |  | 0.74 | 1 | 2596 | EGU | Electric Utility | 4911 | Electric Services | FirstLight Power Resources (Owner/Operator) | [5 empty] | Operating | Combustion turbine | Diesel Oil | [6 empty] | 243
#N/A |  | #N/A |  | 166 | 240 | 60 |  | #N/A |  | #N/A | #N/A | CT | Wallingford Energy, LLC |  | 55517 | CT01 |  | 2010 | CAIROS | 742 | 5 | 31800 |  | 0.02 | 1.6 | 326950 | EGU | Electric Utility | 4911 | Electric Services | PPL Wallingford Energy, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combustion turbine | Pipeline Natural Gas |  |  | Water Injection | Selective Catalytic Reduction |  |  | 530
#N/A |  |  |  | 167 | 238 |  |  | #N/A |  | #N/A | #N/A | CT | Wallingford Energy, LLC |  | 55517 | CT01 |  | 2009 | CAIROS | 239 | 5 | 10326 |  | 0.02 | 0.5 | 101965 | EGU | Electric Utility | 4911 | Electric Services | PPL Wallingford Energy, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combustion turbine | Pipeline Natural Gas |  |  | Water Injection | Selective Catalytic Reduction |  |  | 487.3
#N/A |  |  |  | 168 | 236 |  |  | #N/A |  | #N/A | #N/A | CT | Wallingford Energy, LLC |  | 55517 | CT01 |  | 2008 | CAIROS | 310 | 5 | 13406 |  | 0.02 | 0.7 | 131094 | EGU | Electric Utility | 4911 | Electric Services | PPL Wallingford Energy, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combustion turbine | Pipeline Natural Gas |  |  | Water Injection | Selective Catalytic Reduction |  |  | 461
#N/A |  | #N/A |  | 169 | 246 | 61 |  | #N/A |  | #N/A | #N/A | CT | Wallingford Energy, LLC |  | 55517 | CT02 |  | 2010 | CAIROS | 693 | 5 | 29086 |  | 0.01 | 1.3 | 276159 | EGU | Electric Utility | 4911 | Electric Services | PPL Wallingford Energy, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combustion turbine | Pipeline Natural Gas |  |  | Water Injection | Selective Catalytic Reduction |  |  | 530
#N/A |  |  |  | 170 | 244 |  |  | #N/A |  | #N/A | #N/A | CT | Wallingford Energy, LLC |  | 55517 | CT02 |  | 2009 | CAIROS | 188 | 5 | 7964 |  | 0.01 | 0.3 | 77599 | EGU | Electric Utility | 4911 | Electric Services | PPL Wallingford Energy, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combustion turbine | Pipeline Natural Gas |  |  | Water Injection | Selective Catalytic Reduction |  |  | 487.3
#N/A |  |  |  | 171 | 242 |  |  | #N/A |  | #N/A | #N/A | CT | Wallingford Energy, LLC |  | 55517 | CT02 |  | 2008 | CAIROS | 263 | 5 | 11099 |  | 0.02 | 0.5 | 107867 | EGU | Electric Utility | 4911 | Electric Services | PPL Wallingford Energy, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combustion turbine | Pipeline Natural Gas |  |  | Water Injection | Selective Catalytic Reduction |  |  | 461
#N/A |  | #N/A |  | 172 | 252 | 62 |  | #N/A |  | #N/A | #N/A | CT | Wallingford Energy, LLC |  | 55517 | CT03 |  | 2010 | CAIROS | 546 | 5 | 23858 |  | 0.02 | 1.2 | 234457 | EGU | Electric Utility | 4911 | Electric Services | PPL Wallingford Energy, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combustion turbine | Pipeline Natural Gas |  |  | Water Injection | Selective Catalytic Reduction |  |  | 530
#N/A |  |  |  | 173 | 250 |  |  | #N/A |  | #N/A | #N/A | CT | Wallingford Energy, LLC |  | 55517 | CT03 |  | 2009 | CAIROS | 142 | 5 | 6178 |  | 0.02 | 0.3 | 57960 | EGU | Electric Utility | 4911 | Electric Services | PPL Wallingford Energy, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combustion turbine | Pipeline Natural Gas |  |  | Water Injection | Selective Catalytic Reduction |  |  | 487.3
#N/A |  |  |  | 174 | 248 |  |  | #N/A |  | #N/A | #N/A | CT | Wallingford Energy, LLC |  | 55517 | CT03 |  | 2008 | CAIROS | 155 | 5 | 6577 |  | 0.02 | 0.4 | 63494 | EGU | Electric Utility | 4911 | Electric Services | PPL Wallingford Energy, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combustion turbine | Pipeline Natural Gas |  |  | Water Injection | Selective Catalytic Reduction |  |  | 461
#N/A |  | #N/A |  | 175 | 258 | 63 |  | #N/A |  | #N/A | #N/A | CT | Wallingford Energy, LLC |  | 55517 | CT04 |  | 2010 | CAIROS | 635 | 5 | 27417 |  | 0.01 | 1.2 | 275934 | EGU | Electric Utility | 4911 | Electric Services | PPL Wallingford Energy, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combustion turbine | Pipeline Natural Gas |  |  | Water Injection | Selective Catalytic Reduction |  |  | 530
#N/A |  |  |  | 176 | 256 |  |  | #N/A |  | #N/A | #N/A | CT | Wallingford Energy, LLC |  | 55517 | CT04 |  | 2009 | CAIROS | 270 | 5 | 11686 |  | 0.01 | 0.5 | 107576 | EGU | Electric Utility | 4911 | Electric Services | PPL Wallingford Energy, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combustion turbine | Pipeline Natural Gas |  |  | Water Injection | Selective Catalytic Reduction |  |  | 487.3
#N/A |  |  |  | 177 | 254 |  |  | #N/A |  | #N/A | #N/A | CT | Wallingford Energy, LLC |  | 55517 | CT04 |  | 2008 | CAIROS | 213 | 5 | 8862 |  | 0.02 | 0.5 | 87914 | EGU | Electric Utility | 4911 | Electric Services | PPL Wallingford Energy, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combustion turbine | Pipeline Natural Gas |  |  | Water Injection | Selective Catalytic Reduction |  |  | 461
#N/A |  |  |  | 178 | 264 | 64 |  | #N/A |  | #N/A | #N/A | CT | Wallingford Energy, LLC |  | 55517 | CT05 |  | 2010 | CAIROS | 629 | 5 | 27653 |  | 0.01 | 1.3 | 269839 | EGU | Electric Utility | 4911 | Electric Services | PPL Wallingford Energy, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combustion turbine | Pipeline Natural Gas |  |  | Water Injection | Selective Catalytic Reduction |  |  | 530
#N/A |  |  |  | 179 | 262 |  |  | #N/A |  | #N/A | #N/A | CT | Wallingford Energy, LLC |  | 55517 | CT05 |  | 2009 | CAIROS | 161 | 5 | 6938 |  | 0.01 | 0.3 | 69578 | EGU | Electric Utility | 4911 | Electric Services | PPL Wallingford Energy, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combustion turbine | Pipeline Natural Gas |  |  | Water Injection | Selective Catalytic Reduction |  |  | 487.3
#N/A |  |  |  | 180 | 260 |  |  | #N/A |  | #N/A | #N/A | CT | Wallingford Energy, LLC |  | 55517 | CT05 |  | 2008 | CAIROS | 166 | 5 | 6837 |  | 0.02 | 0.4 | 68816 | EGU | Electric Utility | 4911 | Electric Services | PPL Wallingford Energy, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combustion turbine | Pipeline Natural Gas |  |  | Water Injection | Selective Catalytic Reduction |  |  | 461
#N/A |  |  |  | 181 | 268 | 65 |  | #N/A |  | #N/A | #N/A | CT | Waterbury Generation |  | 56629 | 10 |  | 2010 | CAIROS | 759 | 5 | 65574 |  | 0.02 | 2.9 | 506766 | EGU | Electric Utility |  |  | Waterbury Generation, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating | Combustion turbine | Pipeline Natural Gas | Diesel Oil |  | Water Injection | Selective Catalytic Reduction |  |  | 1800
|  |  |  | 182 | 266 | [6 empty] | CT | Waterbury Generation |  | 56629 | 10 |  | 2009 | CAIROS | 316 | 5 | 20942 |  | 0.06 | 4.6 | 208941 | EGU | Electric Utility |  |  | Waterbury Generation, LLC (Owner/Operator) |  |  |  | Phase 2 |  | Operating (Started 05/15/2009) | Combustion turbine (Started May 15, 2009) | Pipeline Natural Gas | Diesel Oil |  | Water Injection | Selective Catalytic Reduction |  |  | 1800
#N/A |  |  |  | 1: 183; 2: 272; 3: 66; 5: #N/A; 7: #N/A; 8: #N/A; 9: CT; 10: Waterside Power, LLC; 12: 56189; 13: 4; 15: 2010; 16: CAIROS; 17: 68; 18: 5; 21: 0.33; 22: 2.1; 23: 16818; 24: EGU; 25: Electric Utility; 28: Waterside Power, LLC (Owner/Operator); 34: Operating; 35: Combustion turbine; 36: Diesel Oil; 39: Water Injection; 43: 247
#N/A |  |  |  | 1: 184; 2: 271; 5: #N/A; 7: #N/A; 8: #N/A; 9: CT; 10: Waterside Power, LLC; 12: 56189; 13: 4; 15: 2009; 16: CAIROS; 17: 15; 18: 5; 21: 0.6; 22: 0.5; 23: 3636; 24: EGU; 25: Electric Utility; 28: Waterside Power, LLC (Owner/Operator); 34: Operating; 35: Combustion turbine; 36: Diesel Oil; 39: Water Injection; 43: 247
#N/A |  |  |  | 1: 185; 2: 270; 5: #N/A; 7: #N/A; 8: #N/A; 9: CT; 10: Waterside Power, LLC; 12: 56189; 13: 4; 15: 2008; 16: CAIROS; 17: 42; 18: 5; 21: 0.44; 22: 1.3; 23: 10382; 24: EGU; 25: Electric Utility; 28: Waterside Power, LLC (Owner/Operator); 34: Operating; 35: Combustion turbine; 36: Diesel Oil; 39: Water Injection; 43: 247
#N/A |  |  |  | 1: 186; 2: 275; 3: 67; 5: #N/A; 7: #N/A; 8: #N/A; 9: CT; 10: Waterside Power, LLC; 12: 56189; 13: 5; 15: 2010; 16: CAIROS; 17: 73; 18: 5; 21: 0.52; 22: 3.4; 23: 17965; 24: EGU; 25: Electric Utility; 28: Waterside Power, LLC (Owner/Operator); 34: Operating; 35: Combustion turbine; 36: Diesel Oil; 39: Water Injection; 43: 247
#N/A |  |  |  | 1: 187; 2: 274; 5: #N/A; 7: #N/A; 8: #N/A; 9: CT; 10: Waterside Power, LLC; 12: 56189; 13: 5; 15: 2009; 16: CAIROS; 17: 16; 18: 5; 21: 0.56; 22: 0.6; 23: 3841; 24: EGU; 25: Electric Utility; 28: Waterside Power, LLC (Owner/Operator); 34: Operating; 35: Combustion turbine; 36: Diesel Oil; 39: Water Injection; 43: 247
#N/A |  |  |  | 1: 188; 2: 273; 5: #N/A; 7: #N/A; 8: #N/A; 9: CT; 10: Waterside Power, LLC; 12: 56189; 13: 5; 15: 2008; 16: CAIROS; 17: 45; 18: 5; 21: 0.6; 22: 1.7; 23: 11112; 24: EGU; 25: Electric Utility; 28: Waterside Power, LLC (Owner/Operator); 34: Operating; 35: Combustion turbine; 36: Diesel Oil; 39: Water Injection; 43: 247
#N/A |  |  |  | 1: 189; 2: 278; 3: 68; 5: #N/A; 7: #N/A; 8: #N/A; 9: CT; 10: Waterside Power, LLC; 12: 56189; 13: 7; 15: 2010; 16: CAIROS; 17: 69; 18: 5; 21: 0.47; 22: 2.7; 23: 16957; 24: EGU; 25: Electric Utility; 28: Waterside Power, LLC (Owner/Operator); 34: Operating; 35: Combined cycle; 36: Diesel Oil; 39: Water Injection; 43: 247
#N/A |  |  |  | 1: 190; 2: 277; 5: #N/A; 7: #N/A; 8: #N/A; 9: CT; 10: Waterside Power, LLC; 12: 56189; 13: 7; 15: 2009; 16: CAIROS; 17: 16; 18: 5; 21: 0.54; 22: 0.6; 23: 3866; 24: EGU; 25: Electric Utility; 28: Waterside Power, LLC (Owner/Operator); 34: Operating; 35: Combined cycle; 36: Diesel Oil; 39: Water Injection; 43: 247
#N/A |  |  |  | 1: 191; 2: 276; 5: #N/A; 7: #N/A; 8: #N/A; 9: CT; 10: Waterside Power, LLC; 12: 56189; 13: 7; 15: 2008; 16: CAIROS; 17: 44; 18: 5; 21: 0.47; 22: 1.6; 23: 10859; 24: EGU; 25: Electric Utility; 28: Waterside Power, LLC (Owner/Operator); 34: Operating; 35: Combined cycle; 36: Diesel Oil; 39: Water Injection; 43: 247
Unit CAIROS Emissions Report
40688
Your query will return data for 27 facilities and 68 units.
|  |  |  | Unit CAIROS Emissions Report | [8 empty] | You specified: Year(s): 2010,2009,2008 Program: CAIROS State(s): CT
|  |  |  | No. | Seq. | Unit # | TA&O #adj | TA&O # | Rnk | TA&O ID | Unit ID | State | Facility Name | Permit # | Facility ID (ORISPL) | Unit ID | Associated Stacks | Year | Program(s) | Operating Time | # of Months Reported | Gross Load (MWh) | Steam Load (1000 lb) | Avg. NOx Rate (lb/mmBtu) | NOx Tons | Heat Input (mmBtu) | EGU/Non EGU | Source Category | SIC Code | SIC Code Description | Owner Name (Type) | Operator Name (Type) | Representative (Primary) | Representative (Alternate) | SO2 Phase | NOx Phase | Operating Status | Unit Type | Fuel Type(s) (Primary) | Fuel Type(s) (Secondary) | SO2 Control(s) | NOx Control(s) (1) | NOx Control(s) (2) | NOx Control(s) (3) | PM Control(s) | Maximum Heat Input Capacity
REFERENCE ID |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43
|  |  |  | 1 | 3 | 1 |  | #N/A |  |  |  |  | AES Thames |  | 10675 | UNITA | CS01 | 2010 |  | 8442 | 12 |  | 5762995 | 0.06 | 253.1 | 8057126 | EGU |  | 4961 | Steam Supply | AES Corporation (Owner/Operator) | AES Corporation (Owner/Operator) | Boucher, Mark (1767) | Walz, J Andrew (601597) (Ended Nov 23, 2010) |  |  | Operating | Circulating fluidized bed boiler | Coal |  | Fluidized Bed Limestone Injection | Other |  |  | Baghouse | 1045
|  |  |  | 2 | 2 |  |  | #N/A |  |  |  |  | AES Thames |  | 10675 | UNITA | CS01 | 2009 |  | 8322 | 12 |  | 5906894 | 0.06 | 226.3 | 7862908 | EGU |  | 4961 | Steam Supply | AES Corporation (Owner/Operator) | AES Corporation (Owner/Operator) | Boucher, Mark (1767) | Walz, J Andrew (601597) |  |  | Operating | Circulating fluidized bed boiler | Coal |  | Fluidized Bed Limestone Injection | Other |  |  | Baghouse | 1045
|  |  |  | 3 | 1 |  |  | #N/A |  |  |  |  | AES Thames |  | 10675 | UNITA | CS01 | 2008 |  | 8499 | 12 |  | 6008050 | 0.05 | 213.1 | 8257504 | EGU |  | 4961 | Steam Supply | AES Corporation (Owner/Operator) | AES Corporation (Owner/Operator) | Boucher, Mark (1767) (Started Dec 01, 2008) | Walz, J Andrew (601597) (Started Dec 01, 2008) |  |  | Operating | Circulating fluidized bed boiler | Coal |  | Fluidized Bed Limestone Injection | Other |  |  | Baghouse | 1045
|  |  |  | 4 | 6 | 2 |  | #N/A |  |  |  |  | AES Thames |  | 10675 | UNITB | CS01 | 2010 |  | 7838 | 12 |  | 5360533 | 0.06 | 227.2 | 7505560 | EGU |  | 4961 | Steam Supply | AES Corporation (Owner/Operator) | AES Corporation (Owner/Operator) | Boucher, Mark (1767) | Walz, J Andrew (601597) (Ended Nov 23, 2010) |  |  | Operating | Circulating fluidized bed boiler | Coal |  | Fluidized Bed Limestone Injection | Other |  |  | Baghouse | 1045
|  |  |  | 5 | 5 |  |  | #N/A |  |  |  |  | AES Thames |  | 10675 | UNITB | CS01 | 2009 |  | 8118 | 12 |  | 5718691 | 0.06 | 214.9 | 7620536 | EGU |  | 4961 | Steam Supply | AES Corporation (Owner/Operator) | AES Corporation (Owner/Operator) | Boucher, Mark (1767) | Walz, J Andrew (601597) |  |  | Operating | Circulating fluidized bed boiler | Coal |  | Fluidized Bed Limestone Injection | Other |  |  | Baghouse | 1045
|  |  |  | 6 | 4 |  |  | #N/A |  |  |  |  | AES Thames |  | 10675 | UNITB | CS01 | 2008 |  | 8542 | 12 |  | 6048914 | 0.05 | 209.2 | 8319727 | EGU |  | 4961 | Steam Supply | AES Corporation (Owner/Operator) | AES Corporation (Owner/Operator) | Boucher, Mark (1767) (Started Dec 01, 2008) | Walz, J Andrew (601597) (Started Dec 01, 2008) |  |  | Operating | Circulating fluidized bed boiler | Coal |  | Fluidized Bed Limestone Injection | Other |  |  | Baghouse | 1045
|  |  |  | 7 | 9 | 3 |  | #N/A |  |  |  |  | Alfred L Pierce Generating Station |  | 6635 | AP-1 |  | 2010 |  | 80 | 12 | 5228 |  | 0.1 | 4.2 | 85341 | EGU |  |  |  | Connecticut Municipal Electric Energy Coop (Owner/Operator) | Connecticut Municipal Electric Energy Coop (Owner/Operator) | Scully, Maurice (603713) | Stern, Gabriel B (603714) |  |  | Operating | Combustion turbine | Pipeline Natural Gas | Diesel Oil |  | Dry Low NOx Burners | Water Injection |  |  | 1560
|  |  |  | 8 | 8 |  |  | #N/A |  |  |  |  | Alfred L Pierce Generating Station |  | 6635 | AP-1 |  | 2009 |  | 52 | 12 | 3775 |  | 0.1 | 3.3 | 61045 | EGU |  |  |  | Connecticut Municipal Electric Energy Coop (Owner/Operator) | Connecticut Municipal Electric Energy Coop (Owner/Operator) | Scully, Maurice (603713) (Started Jan 30, 2009) | Stern, Gabriel B (603714) (Started Jan 30, 2009) |  |  | Operating | Combustion turbine | Pipeline Natural Gas | Diesel Oil |  | Dry Low NOx Burners | Water Injection |  |  | 1560
|  |  |  | 9 | 7 |  |  | #N/A |  |  |  |  | Alfred L Pierce Generating Station |  | 6635 | AP-1 |  | 2008 |  | 75 | 12 | 4731 |  | 0.13 | 4.3 | 66556 | EGU |  |  |  | Connecticut Municipal Electric Energy Coop (Owner/Operator) | Connecticut Municipal Electric Energy Coop (Owner/Operator) |  |  |  |  | Operating | Combustion turbine | Pipeline Natural Gas | Diesel Oil |  | Dry Low NOx Burners | Water Injection |  |  | 1560
|  |  |  | 10 | 12 | 4 |  | #N/A |  |  |  |  | Algonquin Power Windsor Locks, LLC |  | 10567 | GT1 |  | 2010 |  | 8332 | 12 | 253419 |  | 0.14 | 219.3 | 3171618 | EGU |  | 4911 | Electric Services | Algonquin Power Windsor Locks, LLC (Owner/Operator) | Algonquin Power Windsor Locks, LLC (Owner/Operator) | White, James A (1975) |  |  |  | Operating | Combined cycle | Pipeline Natural Gas | Residual Oil |  | Steam Injection |  |  |  | 555
|  |  |  | 11 | 11 |  |  | #N/A |  |  |  |  | Algonquin Power Windsor Locks, LLC |  | 10567 | GT1 |  | 2009 |  | 8537 | 12 | 311060 |  | 0.14 | 259.1 | 3723099 | EGU |  | 4911 | Electric Services | Algonquin Power Windsor Locks, LLC (Owner/Operator) | Algonquin Power Windsor Locks, LLC (Owner/Operator) | White, James A (1975) |  |  |  | Operating | Combined cycle | Pipeline Natural Gas | Residual Oil |  | Steam Injection |  |  |  | 555
|  |  |  | 12 | 10 |  |  | #N/A |  |  |  |  | Algonquin Power Windsor Locks, LLC |  | 10567 | GT1 |  | 2008 |  | 8710 | 12 | 322573 |  | 0.14 | 265.9 | 3802900 | EGU |  | 4911 | Electric Services | Algonquin Power Windsor Locks, LLC (Owner/Operator) | Algonquin Power Windsor Locks, LLC (Owner/Operator) | White, James A (1975) |  |  |  | Operating | Combined cycle | Pipeline Natural Gas | Residual Oil |  | Steam Injection |  |  |  | 555
8300-01 | NRG | BR10 |  | 13 | 15 | 5 |  | 8300 | 1 | 8300-01 | BR10 |  | Branford |  | 540 | 10 |  | 2010 |  | 39 | 6 | 512 |  | 1.2 | 5.9 | 9750 | EGU |  | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) | Connecticut Jet Power, LLC (Owner/Operator) | Ross, Leslie E (1680) | DesRoberts, David J (604509) |  |  | Operating | Combustion turbine | Other Oil |  |  | Water Injection |  |  |  | 250
|  |  |  | 14 | 14 |  |  | 8300 |  |  |  |  | Branford |  | 540 | 10 |  | 2009 |  | 2 | 6 | 20 |  | 1.2 | 0.3 | 525 | EGU |  | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) | Connecticut Jet Power, LLC (Owner/Operator) | Ross, Leslie E (1680) (Started Dec 28, 2009) | DesRoberts, David J (604509) (Started Dec 28, 2009) |  |  | Operating | Combustion turbine | Other Oil |  |  | Water Injection |  |  |  | 250
|  |  |  | 15 | 13 |  |  | 8300 |  |  |  |  | Branford |  | 540 | 10 |  | 2008 |  | 7 | 6 | 123 |  | 1.2 | 1.1 | 1778 | EGU |  | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) | Connecticut Jet Power, LLC (Owner/Operator) | Carpenter, David M (603378) (Started Nov 17, 2008) | McFalls, Lee E (1678) (Started Nov 17, 2008) |  |  | Operating | Combustion turbine | Other Oil |  |  | Water Injection (Began Jun 01, 2008) |  |  |  | 250
|  |  |  | 16 | 18 | 6 |  | #N/A |  |  |  |  | Bridgeport Energy |  | 55042 | BE1 |  | 2010 |  | 7332 | 12 | 1112541 |  | 0.02 | 88.6 | 11857074 | EGU |  | 4911 | Electric Services | Bridgeport Energy, LLC (Owner/Operator) | Bridgeport Energy, LLC (Owner/Operator) | Callaghan, Daniel J (602048) | French, Kathy (605624) |  |  | Operating | Combined cycle | Pipeline Natural Gas |  |  | Water Injection | Selective Catalytic Reduction |  |  | 1884
|  |  |  | 17 | 17 |  |  | #N/A |  |  |  |  | Bridgeport Energy |  | 55042 | BE1 |  | 2009 |  | 6436 | 12 | 897743 |  | 0.02 | 71.6 | 9670892 | EGU |  | 4911 | Electric Services | Bridgeport Energy, LLC (Owner/Operator) | Bridgeport Energy, LLC (Owner/Operator) | Callaghan, Daniel J (602048) (Started Dec 10, 2009) | French, Kathy (605624) (Started Dec 10, 2009) |  |  | Operating | Combined cycle | Pipeline Natural Gas |  |  | Water Injection | Selective Catalytic Reduction |  |  | 1884
|  |  |  | 18 | 16 |  |  | #N/A |  |  |  |  | Bridgeport Energy |  | 55042 | BE1 |  | 2008 |  | 4634 | 12 | 599482 |  | 0.02 | 57.1 | 6571263 | EGU |  | 4911 | Electric Services | Bridgeport Energy, LLC (Owner/Operator) | Bridgeport Energy, LLC (Owner/Operator) | Klopp, John A (601697) | Dodge, Vincent (2927) |  |  | Operating | Combined cycle | Pipeline Natural Gas |  |  | Water Injection | Selective Catalytic Reduction |  |  | 1884
|  |  |  | 19 | 21 | 7 |  | #N/A |  |  |  |  | Bridgeport Energy |  | 55042 | BE2 |  | 2010 |  | 7217 | 12 | 1089246 |  | 0.02 | 87.8 | 11491142 | EGU |  | 4911 | Electric Services | Bridgeport Energy, LLC (Owner/Operator) | Bridgeport Energy, LLC (Owner/Operator) | Callaghan, Daniel J (602048) | French, Kathy (605624) |  |  | Operating | Combined cycle | Pipeline Natural Gas |  |  | Water Injection | Selective Catalytic Reduction |  |  | 1884
|  |  |  | 20 | 20 |  |  | #N/A |  |  |  |  | Bridgeport Energy |  | 55042 | BE2 |  | 2009 |  | 6159 | 12 | 863661 |  | 0.02 | 74.6 | 9218833 | EGU |  | 4911 | Electric Services | Bridgeport Energy, LLC (Owner/Operator) | Bridgeport Energy, LLC (Owner/Operator) | Callaghan, Daniel J (602048) (Started Dec 10, 2009) | French, Kathy (605624) (Started Dec 10, 2009) |  |  | Operating | Combined cycle | Pipeline Natural Gas |  |  | Water Injection | Selective Catalytic Reduction |  |  | 1884
|  |  |  | 21 | 19 |  |  | #N/A |  |  |  |  | Bridgeport Energy |  | 55042 | BE2 |  | 2008 |  | 5372 | 12 | 707813 |  | 0.02 | 69.4 | 7732619 | EGU |  | 4911 | Electric Services | Bridgeport Energy, LLC (Owner/Operator) | Bridgeport Energy, LLC (Owner/Operator) | Klopp, John A (601697) | Dodge, Vincent (2927) |  |  | Operating | Combined cycle | Pipeline Natural Gas |  |  | Water Injection | Selective Catalytic Reduction |  |  | 1884
|  |  |  | 22 | 22 | 8 | NA | [5 empty] | Bridgeport Harbor Station |  | 568 | BHB1 |  | 2008 |  | 0 | 9 | [5 empty] | EGU |  | 4911 | Electric Services | PSEG (Owner/Operator) (Started Jul 28, 2008) | PSEG (Owner/Operator) (Started Jul 28, 2008) | Wintermeyer, Karl (604377) (Started Jul 28, 2008) | Strickland, Mark F (603622) |  |  | Operating | Cyclone boiler | Residual Oil | Diesel Oil |  |  |  |  | Electrostatic Precipitator | 865
8305-02 | PSEG | BHB2 |  | 23 | 25 | 9 | 4 | 8305 | 2 | 8305-02 | BHB2 |  | Bridgeport Harbor Station | 015-0217-TV | 568 | BHB2 |  | 2010 |  | 157 | 12 | 8430 |  | 0.23 | 14.8 | 105337 | EGU |  | 4911 | Electric Services | PSEG Power Connecticut, LLC (Owner/Operator) | PSEG Power Connecticut, LLC (Owner/Operator) | Stagliola, Michael (604005) | Strickland, Mark F (603622) |  |  | Operating | Cyclone boiler | Residual Oil | Diesel Oil |  |  |  |  | Electrostatic Precipitator | 1785
8305-02 | PSEG | BHB2 |  | 24 | 24 |  | 4 | 8305 | 2 | 8305-02 | BHB2 |  | Bridgeport Harbor Station | 015-0217-TV | 568 | BHB2 |  | 2009 |  | 161 | 12 | 4917 |  | 0.14 | 8.6 | 66280 | EGU |  | 4911 | Electric Services | PSEG Power Connecticut, LLC (Owner/Operator) (Started Oct 14, 2009) | PSEG Power Connecticut, LLC (Owner/Operator) (Started Oct 14, 2009) | Stagliola, Michael (604005) (Started Oct 14, 2009) | Strickland, Mark F (603622) |  |  | Operating | Cyclone boiler | Residual Oil | Diesel Oil |  |  |  |  | Electrostatic Precipitator | 1785
8305-02 | PSEG | BHB2 |  | 25 | 23 |  | 4 | 8305 | 2 | 8305-02 | BHB2 |  | Bridgeport Harbor Station | 015-0217-TV | 568 | BHB2 |  | 2008 |  | 271 | 12 | 8250 |  | 0.21 | 15.1 | 106629 | EGU |  | 4911 | Electric Services | PSEG (Owner/Operator) (Started Jul 28, 2008) | PSEG (Owner/Operator) (Started Jul 28, 2008) | Wintermeyer, Karl (604377) (Started Jul 28, 2008) | Strickland, Mark F (603622) |  |  | Operating | Cyclone boiler | Residual Oil | Diesel Oil |  |  |  |  | Electrostatic Precipitator | 1785
8305-03 | PSEG | BHB3 |  | 26 | 28 | 10 | 4 | 8305 | 3 | 8305-03 | BHB3 |  | Bridgeport Harbor Station | 015-0217-TV | 568 | BHB3 |  | 2010 |  | 4583 | 12 | 1302618 |  | 0.14 | 934.1 | 13168116 | EGU |  | 4911 | Electric Services | PSEG Power Connecticut, LLC (Owner/Operator) | PSEG Power Connecticut, LLC (Owner/Operator) | Stagliola, Michael (604005) | Strickland, Mark F (603622) |  | Early Election | Operating | Tangentially-fired | Coal | Diesel Oil, Residual Oil |  | Low NOx Burner Technology w/ Separated OFA |  |  | Electrostatic Precipitator | 4100
8305-03 | PSEG | BHB3 |  | 27 | 27 |  | 4 | 8305 | 3 | 8305-03 | BHB3 |  | Bridgeport Harbor Station | 015-0217-TV | 568 | BHB3 |  | 2009 |  | 3767 | 12 | 1070682 |  | 0.15 | 838.2 | 11147747 | EGU |  | 4911 | Electric Services | PSEG Power Connecticut, LLC (Owner/Operator) (Started Oct 14, 2009) | PSEG Power Connecticut, LLC (Owner/Operator) (Started Oct 14, 2009) | Stagliola, Michael (604005) (Started Oct 14, 2009) | Strickland, Mark F (603622) |  | Early Election | Operating | Tangentially-fired | Coal | Diesel Oil, Residual Oil |  | Low NOx Burner Technology w/ Separated OFA |  |  | Electrostatic Precipitator | 4100
8305-03 | PSEG | BHB3 |  | 28 | 26 |  | 4 | 8305 | 3 | 8305-03 | BHB3 |  | Bridgeport Harbor Station | 015-0217-TV | 568 | BHB3 |  | 2008 |  | 8303 | 12 | 3010354 |  | 0.14 | 2112.2 | 30494774 | EGU |  | 4911 | Electric Services | PSEG (Owner/Operator) (Started Jul 28, 2008) | PSEG (Owner/Operator) (Started Jul 28, 2008) | Parnell, Robert T (1436) (Started Mar 03, 2008) (Ended Jul 28, 2008) | Strickland, Mark F (603622) |  | Early Election | Operating | Tangentially-fired | Coal | Diesel Oil, Residual Oil |  | Low NOx Burner Technology w/ Separated OFA |  |  | Electrostatic Precipitator | 4100
8301-01 | PSEG | BHB4 |  | 29 | 31 | 11 |  | 8301 | 1 | 8301-01 | BHB4 |  | Bridgeport Harbor Station | 015-0217-TV | 568 | BHB4 |  | 2010 |  | 11 | 6 | 114 |  | 0.71 | 0.7 | 2026 | EGU |  | 4911 | Electric Services | PSEG Power Connecticut, LLC (Owner/Operator) | PSEG Power Connecticut, LLC (Owner/Operator) (Started Oct 14, 2009) | Stagliola, Michael (604005) | Strickland, Mark F (603622) |  |  | Operating | Combustion turbine | Other Oil | [6 empty] | 287
8301-01 | PSEG | BHB4 |  | 30 | 30 |  |  | 8301 | 1 | 8301-01 | BHB4 |  | Bridgeport Harbor Station | 015-0217-TV | 568 | BHB4 |  | 2009 |  | 8 | 6 | 119 |  | 0.67 | 0.7 | 1962 | EGU |  | 4911 | Electric Services | PSEG Power Connecticut, LLC (Owner/Operator) (Started Oct 14, 2009) | PSEG Power Connecticut, LLC (Owner/Operator) (Started Oct 14, 2009) | Stagliola, Michael (604005) (Started Oct 14, 2009) | Strickland, Mark F (603622) |  |  | Operating | Combustion turbine | Other Oil | [6 empty] | 287
8301-01 | PSEG | BHB4 |  | 31 | 29 |  |  | 8301 | 1 | 8301-01 | BHB4 |  | Bridgeport Harbor Station | 015-0217-TV | 568 | BHB4 |  | 2008 |  | 24 | 6 | 105 |  | 0.67 | 0.8 | 2366 | EGU |  | 4911 | Electric Services | PSEG (Owner/Operator) (Started Jul 28, 2008) | PSEG Power Connecticut, LLC (Owner/Operator) (Started Oct 14, 2009) | Parnell, Robert T (1436) (Started Mar 03, 2008) (Ended Jul 28, 2008) | Strickland, Mark F (603622) |  |  | Operating | Combustion turbine | Other Oil | [6 empty] | 287
8298-01 | CDECCA | GT |  | 32 | 34 | 12 |  | 8298 | 1 | 8298-01 | GT |  | Capitol District Energy Center | 075-0064 | 50498 | GT |  | 2010 |  | 308 | 12 | 11458 |  | 0.14 | 5.9 | 103236 | EGU |  | 4961 | Steam Supply | Capitol District Energy Center Cogeneration Assoc. (Owner) | PurEnergy, LLC (Operator) | Bobenic, John (603678) | Wilton, Heather (604203) |  |  | Operating | Combined cycle | Pipeline Natural Gas | Diesel Oil | [5 empty] | 739
8298-01 | CDECCA | GT |  | 33 | 33 |  |  | 8298 | 1 | 8298-01 | GT |  | Capitol District Energy Center | 075-0064 | 50498 | GT |  | 2009 |  | 207 | 12 | 7968 |  | 0.14 | 4.1 | 69014 | EGU |  | 4961 | Steam Supply | Capitol District Energy Center Cogeneration Assoc. (Owner) | PurEnergy, LLC (Operator) | Bobenic, John (603678) | Wilton, Heather (604203) |  |  | Operating | Combined cycle | Pipeline Natural Gas | Diesel Oil | [5 empty] | 739
8298-01 | CDECCA | GT |  | 34 | 32 |  |  | 8298 | 1 | 8298-01 | GT |  | Capitol District Energy Center | 075-0064 | 50498 | GT |  | 2008 |  | 461 | 12 | 21154 |  | 0.14 | 13.2 | 183804 | EGU |  | 4961 | Steam Supply | Capitol District Energy Center Cogeneration Assoc. (Owner) | PurEnergy, LLC (Operator) | Bobenic, John (603678) | Wilton, Heather (604203) (Started Jun 18, 2008) |  |  | Operating | Combined cycle | Pipeline Natural Gas | Diesel Oil | [5 empty] | 739
|  |  |  | 35 | 37 | 13 |  | #N/A |  |  |  |  | Cascades Boxboard Group-Connecticut LLC |  | 54657 | 1 |  | 2010 |  | 8605 | 12 |  | 1252275 | 0.27 | 236.4 | 1725706 | NON EGU |  | 2653 | Corrugated and Solid Fiber Box | Cascades Boxboard Group - Connecticut LLC (Owner/Operator) | Cascades Boxboard Group - Connecticut LLC (Owner/Operator) | Levesque, Ghislain (605616) | Boudreault, Firmin (605617) |  |  | Operating | Dry bottom wall-fired boiler | Pipeline Natural Gas | Residual Oil |  | Low NOx Burner Technology (Dry Bottom only) |  |  |  | 275
|  |  |  | 36 | 36 |  |  | #N/A |  |  |  |  | Cascades Boxboard Group-Connecticut LLC |  | 54657 | 1 |  | 2009 |  | 7882 | 12 |  | 1150270 | 0.23 | 191.8 | 1591452 | NON EGU |  | 2653 | Corrugated and Solid Fiber Box | Cascades Boxboard Group - Connecticut LLC (Owner/Operator) | Cascades Boxboard Group - Connecticut LLC (Owner/Operator) | Levesque, Ghislain (605616) (Started Dec 01, 2009) | Boudreault, Firmin (605617) (Started Dec 01, 2009) |  |  | Operating | Dry bottom wall-fired boiler | Pipeline Natural Gas | Residual Oil |  | Low NOx Burner Technology (Dry Bottom only) |  |  |  | 275
|  |  |  | 37 | 35 |  |  | #N/A |  |  |  |  | Cascades Boxboard Group-Connecticut LLC |  | 54657 | 1 |  | 2008 |  | 7842 | 12 |  | 1021493 | 0.18 | 137.1 | 1398093 | NON EGU |  | 2653 | Corrugated and Solid Fiber Box | Cascades Boxboard Group - Connecticut LLC (Owner/Operator) | Cascades Boxboard Group - Connecticut LLC (Owner/Operator) | LaPorte, Michael (1354) | Dickerson, James (603934) |  |  | Operating | Dry bottom wall-fired boiler | Pipeline Natural Gas | Residual Oil |  | Low NOx Burner Technology (Dry Bottom only) |  |  |  | 275
8300-02 | NRG | CC10 |  | 38 | 40 | 14 |  | 8300 | 2 | 8300-02 | CC10 |  | Cos Cob |  | 542 | 10 |  | 2010 |  | 44 | 6 | 677 |  | 1.2 | 6.6 | 11038 | EGU |  | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) | Connecticut Jet Power, LLC (Owner/Operator) | Ross, Leslie E (1680) | DesRoberts, David J (604509) |  |  | Operating | Combustion turbine | Other Oil |  |  | Water Injection |  |  |  | 250
8300-02 | NRG | CC10 |  | 39 | 39 |  |  | 8300 | 2 | 8300-02 | CC10 |  | Cos Cob |  | 542 | 10 |  | 2009 |  | 8 | 6 | 139 |  | 1.2 | 1.2 | 1968 | EGU |  | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) | Connecticut Jet Power, LLC (Owner/Operator) | Ross, Leslie E (1680) (Started Dec 28, 2009) | DesRoberts, David J (604509) (Started Dec 28, 2009) |  |  | Operating | Combustion turbine | Other Oil |  |  | Water Injection |  |  |  | 250
8300-02 | NRG | CC10 |  | 40 | 38 |  |  | 8300 | 2 | 8300-02 | CC10 |  | Cos Cob |  | 542 | 10 |  | 2008 |  | 11 | 6 | 183 |  | 1.2 | 1.6 | 2740 | EGU |  | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) | Connecticut Jet Power, LLC (Owner/Operator) | Carpenter, David M (603378) (Started Nov 17, 2008) | McFalls, Lee E (1678) (Started Nov 17, 2008) |  |  | Operating | Combustion turbine | Other Oil |  |  | Water Injection (Began Jul 01, 2008) |  |  |  | 250
8300-03 | NRG | CC11 |  | 41 | 43 | 15 |  | 8300 | 3 | 8300-03 | CC11 |  | Cos Cob |  | 542 | 11 |  | 2010 |  | 40 | 6 | 619 |  | 1.2 | 6.1 | 10085 | EGU |  | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) | Connecticut Jet Power, LLC (Owner/Operator) | Ross, Leslie E (1680) | DesRoberts, David J (604509) |  |  | Operating | Combustion turbine | Other Oil |  |  | Water Injection |  |  |  | 250
8300-03 | NRG | CC11 |  | 42 | 42 |  |  | 8300 | 3 | 8300-03 | CC11 |  | Cos Cob |  | 542 | 11 |  | 2009 |  | 6 | 6 | 102 |  | 1.2 | 0.9 | 1465 | EGU |  | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) | Connecticut Jet Power, LLC (Owner/Operator) | Ross, Leslie E (1680) (Started Dec 28, 2009) | DesRoberts, David J (604509) (Started Dec 28, 2009) |  |  | Operating | Combustion turbine | Other Oil |  |  | Water Injection |  |  |  | 250
8300-03 | NRG | CC11 |  | 43 | 41 |  |  | 8300 | 3 | 8300-03 | CC11 |  | Cos Cob |  | 542 | 11 |  | 2008 |  | 9 | 6 | 160 |  | 1.2 | 1.3 | 2225 | EGU |  | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) | Connecticut Jet Power, LLC (Owner/Operator) | Carpenter, David M (603378) (Started Nov 17, 2008) | McFalls, Lee E (1678) (Started Nov 17, 2008) |  |  | Operating | Combustion turbine | Other Oil |  |  | Water Injection (Began Jul 01, 2008) |  |  |  | 250
8300-04 | NRG | CC12 |  | 44 | 46 | 16 |  | 8300 | 4 | 8300-04 | CC12 |  | Cos Cob |  | 542 | 12 |  | 2010 |  | 51 | 6 | 790 |  | 1.2 | 7.7 | 12848 | EGU |  | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) | Connecticut Jet Power, LLC (Owner/Operator) | Ross, Leslie E (1680) | DesRoberts, David J (604509) |  |  | Operating | Combustion turbine | Other Oil |  |  | Water Injection |  |  |  | 250
8300-04 | NRG | CC12 |  | 45 | 45 |  |  | 8300 | 4 | 8300-04 | CC12 |  | Cos Cob |  | 542 | 12 |  | 2009 |  | 7 | 6 | 131 |  | 1.2 | 1.1 | 1780 | EGU |  | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) | Connecticut Jet Power, LLC (Owner/Operator) | Ross, Leslie E (1680) (Started Dec 28, 2009) | DesRoberts, David J (604509) (Started Dec 28, 2009) |  |  | Operating | Combustion turbine | Other Oil |  |  | Water Injection |  |  |  | 250
8300-04 | NRG | CC12 |  | 46 | 44 |  |  | 8300 | 4 | 8300-04 | CC12 |  | Cos Cob |  | 542 | 12 |  | 2008 |  | 6 | 6 | 115 |  | 1.2 | 1 | 1595 | EGU |  | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) | Connecticut Jet Power, LLC (Owner/Operator) |  |  |  |  | Operating | Combustion turbine | Other Oil |  |  | Water Injection (Began Jul 01, 2008) |  |  |  | 250
8300-05 | NRG | CC13 |  | 47 | 49 | 17 |  | 8300 | 5 | 8300-05 | CC13 |  | Cos Cob |  | 542 | 13 |  | 2010 |  | 35 | 6 | 476 |  | 1.2 | 6.5 | 10832 | EGU |  | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) | Connecticut Jet Power, LLC (Owner/Operator) | Ross, Leslie E (1680) | DesRoberts, David J (604509) |  |  | Operating | Combustion turbine | Other Oil |  |  | Water Injection |  |  |  | 308
8300-05 | NRG | CC13 |  | 48 | 48 |  |  | 8300 | 5 | 8300-05 | CC13 |  | Cos Cob |  | 542 | 13 |  | 2009 |  | 8 | 6 | 155 |  | 1.2 | 1.6 | 2602 | EGU |  | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) | Connecticut Jet Power, LLC (Owner/Operator) | Ross, Leslie E (1680) (Started Dec 28, 2009) | DesRoberts, David J (604509) (Started Dec 28, 2009) |  |  | Operating | Combustion turbine | Other Oil |  |  | Water Injection |  |  |  | 308
8300-05 | NRG | CC13 |  | 1: 49; 2: 47; 5: 8300; 6: 5; 7: 8300-05; 8: CC13; 10: Cos Cob; 12: 542; 13: 13; 15: 2008; 17: 4; 18: 6; 19: 93; 21: 1.2; 22: 0.8; 23: 1368; 24: EGU; 26: 4911; 27: Electric Services; 34: Operating (Started 06/16/2008); 35: Combustion turbine (Started Jun 01, 2008); 36: Other Oil; 39: Water Injection (Began Jun 16, 2008); 43: 308
8300-06 | NRG | CC14 |  | 50 | 52 | 18 |  | 8300 | 6 | 8300-06 | CC14 |  | Cos Cob |  | 542 | 14 |  | 2010 |  | 42 | 6 | 604 |  | 1.2 | 7.8 | 12967 | EGU |  | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) | Connecticut Jet Power, LLC (Owner/Operator) | Ross, Leslie E (1680) | DesRoberts, David J (604509) |  |  | Operating | Combustion turbine | Other Oil |  |  | Water Injection |  |  |  | 308
8300-06 | NRG | CC14 |  | 51 | 51 |  |  | 8300 | 6 | 8300-06 | CC14 |  | Cos Cob |  | 542 | 14 |  | 2009 |  | 13 | 6 | 209 |  | 1.2 | 2.5 | 4118 | EGU |  | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) | Connecticut Jet Power, LLC (Owner/Operator) | Ross, Leslie E (1680) (Started Dec 28, 2009) | DesRoberts, David J (604509) (Started Dec 28, 2009) |  |  | Operating | Combustion turbine | Other Oil |  |  | Water Injection |  |  |  | 308
8300-06 | NRG | CC14 |  | 52 | 50 |  |  | 8300 | 6 | 8300-06 | CC14 |  | Cos Cob |  | 542 | 14 |  | 2008 |  | 4 | 6 | 91 |  | 1.2 | 0.8 | 1334 | EGU |  | 4911 | Electric Services |  |  | Carpenter, David M (603378) (Started Nov 17, 2008) | McFalls, Lee E (1678) (Started Nov 17, 2008) |  |  | Operating (Started 06/19/2008) | Combustion turbine (Started Jun 01, 2008) | Other Oil |  |  | Water Injection (Began Jun 19, 2008) |  |  |  | 308
8300-11 | NRG | DV10 |  | 53 | 55 | 19 |  | 8300 | 11 | 8300-11 | DV10 |  | Devon |  | 544 | 10 |  | 2010 |  | 24 | 6 | 454 |  | 1.2 | 3.3 | 5575 | EGU |  | 4911 | Electric Services | Devon Power, LLC (Owner/Operator) | Devon Power, LLC (Owner/Operator) | Ross, Leslie E (1680) | McFalls, Lee E (1678) |  |  | Operating | Combustion turbine | Other Oil | [6 empty] | 230
8300-11 | NRG | DV10 |  | 54 | 54 |  |  | 8300 | 11 | 8300-11 | DV10 |  | Devon |  | 544 | 10 |  | 2009 |  | 4 | 6 | 65 |  | 1.2 | 0.5 | 869 | EGU |  | 4911 | Electric Services | Devon Power, LLC (Owner/Operator) | Devon Power, LLC (Owner/Operator) | Ross, Leslie E (1680) | McFalls, Lee E (1678) |  |  | Operating | Combustion turbine | Other Oil | [6 empty] | 230
8300-11 | NRG | DV10 |  | 1: 55; 2: 53; 5: 8300; 6: 11; 7: 8300-11; 8: DV10; 10: Devon; 12: 544; 13: 10; 15: 2008; 17: 6; 18: 6; 19: 112; 21: 1.2; 22: 0.8; 23: 1352; 24: EGU; 26: 4911; 27: Electric Services; 28: Devon Power, LLC (Owner/Operator); 29: Devon Power, LLC (Owner/Operator); 34: Operating; 35: Combustion turbine; 36: Other Oil; 43: 230
8300-12 | NRG | DV11 |  | 56 | 58 | 20 |  | 8300 | 12 | 8300-12 | DV11 |  | Devon |  | 544 | 11 |  | 2010 |  | 107 | 12 | 3341 |  | 0.15 | 2.6 | 34493 | EGU |  | 4911 | Electric Services | Devon Power, LLC (Owner/Operator) | Devon Power, LLC (Owner/Operator) | Ross, Leslie E (1680) | McFalls, Lee E (1678) |  |  | Operating | Combustion turbine | Pipeline Natural Gas | Other Oil |  | Water Injection |  |  |  | 415
8300-12 | NRG | DV11 |  | 57 | 57 |  |  | 8300 | 12 | 8300-12 | DV11 |  | Devon |  | 544 | 11 |  | 2009 |  | 70 | 12 | 2387 |  | 0.16 | 2 | 24111 | EGU |  | 4911 | Electric Services | Devon Power, LLC (Owner/Operator) | Devon Power, LLC (Owner/Operator) | Ross, Leslie E (1680) | McFalls, Lee E (1678) |  |  | Operating | Combustion turbine | Pipeline Natural Gas | Other Oil |  | Water Injection |  |  |  | 415
8300-12 | NRG | DV11 |  | 58 | 56 |  |  | 8300 | 12 | 8300-12 | DV11 |  | Devon |  | 544 | 11 |  | 2008 |  | 38 | 12 | 1181 |  | 0.16 | 1 | 12062 | EGU |  | 4911 | Electric Services | Devon Power, LLC (Owner/Operator) | Devon Power, LLC (Owner/Operator) | Ross, Leslie E (1680) (Started Nov 17, 2008) | McFalls, Lee E (1678) (Started Nov 17, 2008) |  |  | Operating | Combustion turbine | Pipeline Natural Gas | Other Oil |  | Water Injection |  |  |  | 415
8300-13 | NRG | DV12 |  | 59 | 61 | 21 |  | 8300 | 13 | 8300-13 | DV12 |  | Devon |  | 544 | 12 |  | 2010 |  | 79 | 12 | 2531 |  | 0.13 | 1.7 | 25823 | EGU |  | 4911 | Electric Services | Devon Power, LLC (Owner/Operator) | Devon Power, LLC (Owner/Operator) | Ross, Leslie E (1680) | McFalls, Lee E (1678) |  |  | Operating | Combustion turbine | Pipeline Natural Gas | Other Oil |  | Water Injection |  |  |  | 415
8300-13 | NRG | DV12 |  | 60 | 60 |  |  | 8300 | 13 | 8300-13 | DV12 |  | Devon |  | 544 | 12 |  | 2009 |  | 66 | 12 | 2202 |  | 0.13 | 1.5 | 22459 | EGU |  | 4911 | Electric Services | Devon Power, LLC (Owner/Operator) | Devon Power, LLC (Owner/Operator) | Ross, Leslie E (1680) | McFalls, Lee E (1678) |  |  | Operating | Combustion turbine | Pipeline Natural Gas | Other Oil |  | Water Injection |  |  |  | 415
8300-13 | NRG | DV12 |  | 61 | 59 |  |  | 8300 | 13 | 8300-13 | DV12 |  | Devon |  | 544 | 12 |  | 2008 |  | 37 | 12 | 1155 |  | 0.13 | 0.9 | 12576 | EGU |  | 4911 | Electric Services | Devon Power, LLC (Owner/Operator) | Devon Power, LLC (Owner/Operator) | Ross, Leslie E (1680) (Started Nov 17, 2008) | McFalls, Lee E (1678) (Started Nov 17, 2008) |  |  | Operating | Combustion turbine | Pipeline Natural Gas | Other Oil |  | Water Injection |  |  |  | 415
8300-14 | NRG | DV13 |  | 62 | 64 | 22 |  | 8300 | 14 | 8300-14 | DV13 |  | Devon |  | 544 | 13 |  | 2010 |  | 114 | 12 | 3634 |  | 0.15 | 3 | 37637 | EGU |  | 4911 | Electric Services | Devon Power, LLC (Owner/Operator) | Devon Power, LLC (Owner/Operator) | Ross, Leslie E (1680) | McFalls, Lee E (1678) |  |  | Operating | Combustion turbine | Pipeline Natural Gas | Other Oil |  | Water Injection |  |  |  | 415
8300-14 | NRG | DV13 |  | 63 | 63 |  |  | 8300 | 14 | 8300-14 | DV13 |  | Devon |  | 544 | 13 |  | 2009 |  | 93 | 12 | 3120 |  | 0.15 | 2.5 | 31591 | EGU |  | 4911 | Electric Services | Devon Power, LLC (Owner/Operator) | Devon Power, LLC (Owner/Operator) | Ross, Leslie E (1680) | McFalls, Lee E (1678) |  |  | Operating | Combustion turbine | Pipeline Natural Gas | Other Oil |  | Water Injection |  |  |  | 415
8300-14 | NRG | DV13 |  | 64 | 62 |  |  | 8300 | 14 | 8300-14 | DV13 |  | Devon |  | 544 | 13 |  | 2008 |  | 44 | 12 | 1419 |  | 0.16 | 1.2 | 14561 | EGU |  | 4911 | Electric Services | Devon Power, LLC (Owner/Operator) | Devon Power, LLC (Owner/Operator) | Ross, Leslie E (1680) (Started Nov 17, 2008) | McFalls, Lee E (1678) (Started Nov 17, 2008) |  |  | Operating | Combustion turbine | Pipeline Natural Gas | Other Oil |  | Water Injection |  |  |  | 415
8300-15 | NRG | DV14 |  | 65 | 67 | 23 |  | 8300 | 15 | 8300-15 | DV14 |  | Devon |  | 544 | 14 |  | 2010 |  | 131 | 12 | 4136 |  | 0.15 | 3.3 | 41882 | EGU |  | 4911 | Electric Services | Devon Power, LLC (Owner/Operator) | Devon Power, LLC (Owner/Operator) | Ross, Leslie E (1680) | McFalls, Lee E (1678) |  |  | Operating | Combustion turbine | Pipeline Natural Gas | Other Oil |  | Water Injection |  |  |  | 415
|  |  |  | 66 | 66 |  |  |  | 15 |  |  |  | Devon |  | 544 | 14 |  | 2009 |  | 91 | 12 | 3150 |  | 0.16 | 2.6 | 31304 | EGU |  | 4911 | Electric Services | Devon Power, LLC (Owner/Operator) | Devon Power, LLC (Owner/Operator) | Ross, Leslie E (1680) | McFalls, Lee E (1678) |  |  | Operating | Combustion turbine | Pipeline Natural Gas | Other Oil |  | Water Injection |  |  |  | 415
|  |  |  | 67 | 65 |  |  |  | 15 |  |  |  | Devon |  | 544 | 14 |  | 2008 |  | 39 | 12 | 1247 |  | 0.15 | 1 | 12495 | EGU |  | 4911 | Electric Services | Devon Power, LLC (Owner/Operator) | Devon Power, LLC (Owner/Operator) | Ross, Leslie E (1680) (Started Nov 17, 2008) | McFalls, Lee E (1678) (Started Nov 17, 2008) |  |  | Operating | Combustion turbine | Pipeline Natural Gas | Other Oil |  | Water Injection |  |  |  | 415
|  |  |  | 68 | 68 | 24 | NA | [5 empty] | Devon |  | 544 | 15 |  | 2010 |  | 13 | 6 | 497 |  | 0.02 | 0 | 4857 | EGU |  | 4911 | Electric Services | GenConn Devon LLC (Owner) | Devon Power, LLC (Operator) | Ross, Leslie E (1680) | McFalls, Lee E (1678) |  |  | Operating (Started 07/10/2010) | Combustion turbine (Started Jul 10, 2010) | Other Oil | Pipeline Natural Gas |  | Water Injection | Selective Catalytic Reduction |  |  | 474.9
|  |  |  | 69 | 69 | 25 | NA | [5 empty] | Devon |  | 544 | 16 |  | 2010 |  | 11 | 6 | 470 |  | 0.02 | 0 | 4333 | EGU |  | 4911 | Electric Services | GenConn Devon LLC (Owner) | Devon Power, LLC (Operator) | Ross, Leslie E (1680) | McFalls, Lee E (1678) |  |  | Operating (Started 06/25/2010) | Combustion turbine (Started Jun 25, 2010) | Other Oil | Pipeline Natural Gas |  | Water Injection | Selective Catalytic Reduction |  |  | 589
|  |  |  | 70 | 70 | 26 | NA | [5 empty] | Devon |  | 544 | 17 |  | 2010 |  | 14 | 6 | 631 |  | 0.01 | 0 | 5783 | EGU |  | 4911 | Electric Services | GenConn Devon LLC (Owner) | Devon Power, LLC (Operator) | Ross, Leslie E (1680) | McFalls, Lee E (1678) |  |  | Operating (Started 06/10/2010) | Combustion turbine (Started Jun 10, 2010) | Other Oil | Pipeline Natural Gas |  | Water Injection | Selective Catalytic Reduction |  |  | 590.6
|  |  |  | 71 | 71 | 27 | NA | [5 empty] | Devon |  | 544 | 18 |  | 2010 |  | 12 | 6 | 464 |  | 0.02 | 0 | 4541 | EGU |  | 4911 | Electric Services | GenConn Devon LLC (Owner) | Devon Power, LLC (Operator) | Ross, Leslie E (1680) | McFalls, Lee E (1678) |  |  | Operating (Started 06/01/2010) | Combustion turbine (Started Jun 01, 2010) | Other Oil | Pipeline Natural Gas |  | Water Injection | Selective Catalytic Reduction |  |  | 590
#N/A | #N/A | #N/A |  | 72 | 74 | 28 |  | #N/A |  | #N/A | #N/A |  | Exeter Energy Limited Partnership |  | 50736 | B1 | CS1 | 2010 |  | 3190 | 6 |  | 401260 | 0.12 | 39.8 | 679481 | EGU |  |  |  | Exeter Energy Limited Partnership (Owner/Operator) | Exeter Energy Limited Partnership (Owner/Operator) | Martin, Marsal (604847) | Harnsberger, Thomas M (605646) |  |  | Operating | Stoker | Tire Derived Fuel | Liquified Petroleum Gas | [5 empty] | 181
#N/A | #N/A | #N/A |  | 73 | 73 |  |  | #N/A |  | #N/A | #N/A |  | Exeter Energy Limited Partnership |  | 50736 | B1 | CS1 | 2009 |  | 2885 | 6 |  | 324373 | 0.1 | 21.2 | 440239 | EGU |  |  |  | Exeter Energy Limited Partnership (Owner/Operator) | Exeter Energy Limited Partnership (Owner/Operator) | Martin, Marsal (604847) (Started Dec 30, 2009) | Harnsberger, Thomas M (605646) (Started Dec 30, 2009) |  |  | Operating | Stoker (Started Jan 07, 2009), Other boiler (Ended Jan 07, 2009) | Tire Derived Fuel | Liquified Petroleum Gas | [5 empty] | 181
#N/A | #N/A | #N/A |  | 1: 74; 2: 72; 5: #N/A; 7: #N/A; 8: #N/A; 10: Exeter Energy Limited Partnership; 12: 50736; 13: B1; 14: CS1; 15: 2008; 17: 2842; 18: 6; 20: 324972; 21: 0.11; 22: 48; 23: 913123; 24: EGU; 28: Exeter Energy Limited Partnership (Owner/Operator) (Started Feb 19, 2008); 30: Wycherley, Kenneth (604041) (Started Feb 19, 2008); 34: Operating; 35: Other boiler; 36: Tire Derived Fuel; 37: Liquified Petroleum Gas; 43: 181
#N/A | #N/A | #N/A |  | 75 | 77 | 29 |  | #N/A |  | #N/A | #N/A |  | Exeter Energy Limited Partnership |  | 50736 | B2 | CS1 | 2010 |  | 3494 | 6 |  | 436752 | 0.12 | 43.5 | 744972 | EGU |  |  |  | Exeter Energy Limited Partnership (Owner/Operator) | Exeter Energy Limited Partnership (Owner/Operator) | Martin, Marsal (604847) | Harnsberger, Thomas M (605646) |  |  | Operating | Stoker | Tire Derived Fuel | Liquified Petroleum Gas | [5 empty] | 181
#N/A | #N/A | #N/A |  | 76 | 76 |  |  | #N/A |  | #N/A | #N/A |  | Exeter Energy Limited Partnership |  | 50736 | B2 | CS1 | 2009 |  | 2936 | 6 |  | 326730 | 0.11 | 21.4 | 446393 | EGU |  |  |  | Exeter Energy Limited Partnership (Owner/Operator) | Exeter Energy Limited Partnership (Owner/Operator) | Martin, Marsal (604847) (Started Dec 30, 2009) | Harnsberger, Thomas M (605646) (Started Dec 30, 2009) |  |  | Operating | Stoker (Started Jan 07, 2009), Other boiler (Ended Jan 07, 2009) | Tire Derived Fuel | Liquified Petroleum Gas | [5 empty] | 181
#N/A | #N/A | #N/A |  | 1: 77; 2: 75; 5: #N/A; 7: #N/A; 8: #N/A; 10: Exeter Energy Limited Partnership; 12: 50736; 13: B2; 14: CS1; 15: 2008; 17: 2908; 18: 6; 20: 336464; 21: 0.11; 22: 61.4; 23: 1167796; 24: EGU; 28: Exeter Energy Limited Partnership (Owner/Operator) (Started Feb 19, 2008); 29: Exeter Energy Limited Partnership (Owner/Operator) (Started Feb 19, 2008); 30: Wycherley, Kenneth (604041) (Started Feb 19, 2008); 34: Operating; 35: Other boiler; 36: Tire Derived Fuel; 37: Liquified Petroleum Gas; 43: 181
8300-07 | NRG | FD10 |  | 78 | 80 | 30 |  | 8300 | 7 | 8300-07 | FD10 |  | Franklin Drive |  | 561 | 10 |  | 2010 |  | 46 | 6 | 639 |  | 1.2 | 6.9 | 11515 | EGU |  | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) | Connecticut Jet Power, LLC (Owner/Operator) | Ross, Leslie E (1680) | DesRoberts, David J (604509) |  |  | Operating | Combustion turbine | Other Oil | [6 empty] | 250
8300-07 | NRG | FD10 |  | 79 | 79 |  |  | 8300 | 7 | 8300-07 | FD10 |  | Franklin Drive |  | 561 | 10 |  | 2009 |  | 5 | 6 | 62 |  | 1.2 | 0.7 | 1145 | EGU |  | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) | Connecticut Jet Power, LLC (Owner/Operator) | Ross, Leslie E (1680) (Started Dec 28, 2009) | DesRoberts, David J (604509) (Started Dec 28, 2009) |  |  | Operating | Combustion turbine | Other Oil | [6 empty] | 250
8300-07 | NRG | FD10 |  | 80 | 78 |  |  | 8300 | 7 | 8300-07 | FD10 |  | Franklin Drive |  | 561 | 10 |  | 2008 |  | 8 | 6 | 142 |  | 1.2 | 1.2 | 2060 | EGU |  | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) | Connecticut Jet Power, LLC (Owner/Operator) | Carpenter, David M (603378) (Started Nov 17, 2008) | McFalls, Lee E (1678) (Started Nov 17, 2008) |  |  | Operating | Combustion turbine | Other Oil | [6 empty] | 250
#N/A | #N/A | #N/A |  | 81 | 83 | 31 |  | #N/A |  | #N/A | #N/A |  | Lake Road Generating Company |  | 55149 | LRG1 |  | 2010 |  | 5505 | 12 | 849690 |  | 0.01 | 33.1 | 9159016 | EGU |  | 4911 | Electric Services | Lake Road Generating Company, LP (Owner/Operator) | Lake Road Generating Company, LP (Owner/Operator) | Curtis, Christopher J (602681) (Started Jun 21, 2010) | Neil, John S (604756) (Started Jun 21, 2010) |  |  | Operating | Combined cycle | Pipeline Natural Gas | Diesel Oil |  | Dry Low NOx Burners | Water Injection | Selective Catalytic Reduction |  | 2276
#N/A | #N/A | #N/A |  | 82 | 82 |  |  | #N/A |  | #N/A | #N/A |  | Lake Road Generating Company |  | 55149 | LRG1 |  | 2009 |  | 4567 | 12 | 680126 |  | 0.01 | 26.7 | 7405915 | EGU |  | 4911 | Electric Services | Lake Road Generating Company, LP (Owner/Operator) | Lake Road Generating Company, LP (Owner/Operator) | Neil, John S (604756) (Started Apr 01, 2009) | Curtis, Christopher J (602681) (Started Sep 01, 2009) |  |  | Operating | Combined cycle | Pipeline Natural Gas | Diesel Oil |  | Dry Low NOx Burners | Water Injection | Selective Catalytic Reduction |  | 2276
#N/A | #N/A | #N/A |  | 83 | 81 |  |  | #N/A |  | #N/A | #N/A |  | Lake Road Generating Company |  | 55149 | LRG1 |  | 2008 |  | 3321 | 12 | 479170 |  | 0.01 | 20.8 | 5311245 | EGU |  | 4911 | Electric Services | Lake Road Generating Company, LP (Owner/Operator) | Lake Road Generating Company, LP (Owner/Operator) | Haley, Robert B (603503) | Neil, John S (604756) (Started Dec 04, 2008) |  |  | Operating | Combined cycle | Pipeline Natural Gas | Diesel Oil |  | Dry Low NOx Burners | Water Injection | Selective Catalytic Reduction |  | 2276
#N/A | #N/A | #N/A |  | 84 | 86 | 32 |  | #N/A |  | #N/A | #N/A |  | Lake Road Generating Company |  | 55149 | LRG2 |  | 2010 |  | 5293 | 12 | 831134 |  | 0.01 | 33.2 | 8885452 | EGU |  | 4911 | Electric Services | Lake Road Generating Company, LP (Owner/Operator) | Lake Road Generating Company, LP (Owner/Operator) | Curtis, Christopher J (602681) (Started Jun 21, 2010) | Neil, John S (604756) (Started Jun 21, 2010) |  |  | Operating | Combined cycle | Pipeline Natural Gas | Diesel Oil |  | Dry Low NOx Burners | Water Injection | Selective Catalytic Reduction |  | 2276
#N/A | #N/A | #N/A |  | 85 | 85 |  |  | #N/A |  | #N/A | #N/A |  | Lake Road Generating Company |  | 55149 | LRG2 |  | 2009 |  | 4249 | 12 | 632605 |  | 0.01 | 27.4 | 6802198 | EGU |  | 4911 | Electric Services | Lake Road Generating Company, LP (Owner/Operator) | Lake Road Generating Company, LP (Owner/Operator) | Neil, John S (604756) (Started Apr 01, 2009) | Curtis, Christopher J (602681) (Started Sep 01, 2009) |  |  | Operating | Combined cycle | Pipeline Natural Gas | Diesel Oil |  | Dry Low NOx Burners | Water Injection | Selective Catalytic Reduction |  | 2276
#N/A | #N/A | #N/A |  | 86 | 84 |  |  | #N/A |  | #N/A | #N/A |  | Lake Road Generating Company |  | 55149 | LRG2 |  | 2008 |  | 4262 | 12 | 650810 |  | 0.02 | 30.4 | 6973951 | EGU |  | 4911 | Electric Services | Lake Road Generating Company, LP (Owner/Operator) | Lake Road Generating Company, LP (Owner/Operator) | Haley, Robert B (603503) | Neil, John S (604756) (Started Dec 04, 2008) |  |  | Operating | Combined cycle | Pipeline Natural Gas | Diesel Oil |  | Dry Low NOx Burners | Water Injection | Selective Catalytic Reduction |  | 2276
#N/A | #N/A | #N/A |  | 87 | 89 | 33 |  | #N/A |  | #N/A | #N/A |  | Lake Road Generating Company |  | 55149 | LRG3 |  | 2010 |  | 5239 | 12 | 829023 |  | 0.01 | 27.5 | 8927591 | EGU |  | 4911 | Electric Services | Lake Road Generating Company, LP (Owner/Operator) | Lake Road Generating Company, LP (Owner/Operator) | Curtis, Christopher J (602681) (Started Jun 21, 2010) | Neil, John S (604756) (Started Jun 21, 2010) |  |  | Operating | Combined cycle | Pipeline Natural Gas | Diesel Oil |  | Dry Low NOx Burners | Water Injection | Selective Catalytic Reduction |  | 2276
#N/A | #N/A | #N/A |  | 88 | 88 |  |  | #N/A |  | #N/A | #N/A |  | Lake Road Generating Company |  | 55149 | LRG3 |  | 2009 |  | 3364 | 12 | 491589 |  | 0.02 | 22 | 5441846 | EGU |  | 4911 | Electric Services | Lake Road Generating Company, LP (Owner/Operator) | Lake Road Generating Company, LP (Owner/Operator) | Neil, John S (604756) (Started Apr 01, 2009) | Curtis, Christopher J (602681) (Started Sep 01, 2009) |  |  | Operating | Combined cycle | Pipeline Natural Gas | Diesel Oil |  | Dry Low NOx Burners | Water Injection | Selective Catalytic Reduction |  | 2276
#N/A | #N/A | #N/A |  | 89 | 87 |  |  | #N/A |  | #N/A | #N/A |  | Lake Road Generating Company |  | 55149 | LRG3 |  | 2008 |  | 3904 | 12 | 599777 |  | 0.02 | 26.8 | 6648893 | EGU |  | 4911 | Electric Services | Lake Road Generating Company, LP (Owner/Operator) | Lake Road Generating Company, LP (Owner/Operator) | Haley, Robert B (603503) | Neil, John S (604756) (Started Dec 04, 2008) |  |  | Operating | Combined cycle | Pipeline Natural Gas | Diesel Oil |  | Dry Low NOx Burners | Water Injection | Selective Catalytic Reduction |  | 2276
8300-09 | NRG | MD10 |  | 90 | 92 | 34 |  | 8300 | 9 | 8300-09 | MD10 |  | Middletown |  | 562 | 10 |  | 2010 |  | 95 | 6 | 1275 |  | 1.2 | 14.3 | 23750 | EGU |  | 4911 | Electric Services | Middletown Power, LLC (Owner/Operator) | Middletown Power, LLC (Owner/Operator) | DesRoberts, David J (604509) | McFalls, Lee E (1678) (Started Feb 26, 2010) |  |  | Operating | Combustion turbine | Other Oil | [6 empty] | 250
8300-09 | NRG | MD10 |  | 91 | 91 |  |  | 8300 | 9 | 8300-09 | MD10 |  | Middletown |  | 562 | 10 |  | 2009 |  | 20 | 6 | 243 |  | 1.2 | 3 | 5013 | EGU |  | 4911 | Electric Services | Middletown Power, LLC (Owner/Operator) (Started Apr 08, 2009) | Middletown Power, LLC (Owner/Operator) (Started Apr 08, 2009) | DesRoberts, David J (604509) (Started Apr 07, 2009) | Ariagno, Leonard J (646) (Started Nov 20, 2009) |  |  | Operating | Combustion turbine | Other Oil | [6 empty] | 250
8300-09 | NRG | MD10 |  | 92 | 90 |  |  | 8300 | 9 | 8300-09 | MD10 |  | Middletown |  | 562 | 10 |  | 2008 |  | 17 | 6 | 405 |  | 1.2 | 2.6 | 4250 | EGU |  | 4911 | Electric Services | Middletown Power, LLC (Owner) | NRG Energy, Inc (Operator) | Carpenter, David M (603378) | McFalls, Lee E (1678) |  |  | Operating | Combustion turbine | Other Oil | [6 empty] | 250
8306-01 | NRG | MD2 |  | 93 | 95 | 35 | 6 | 8306 | 1 | 8306-01 | MD2 |  | Middletown |  | 562 | 2 |  | 2010 |  | 2181 | 12 | 124995 |  | 0.12 | 107.3 | 1620374 | EGU |  | 4911 | Electric Services | Middletown Power, LLC (Owner/Operator) | Middletown Power, LLC (Owner/Operator) | DesRoberts, David J (604509) | McFalls, Lee E (1678) (Started Feb 26, 2010) |  |  | Operating | Dry bottom wall-fired boiler | Residual Oil | Pipeline Natural Gas |  | Overfire Air |  |  | Electrostatic Precipitator | 1295
8306-01 | NRG | MD2 |  | 94 | 94 |  | 6 | 8306 | 1 | 8306-01 | MD2 |  | Middletown |  | 562 | 2 |  | 2009 |  | 1196 | 12 | 66397 |  | 0.13 | 66.7 | 878712 | EGU |  | 4911 | Electric Services | Middletown Power, LLC (Owner/Operator) (Started Apr 07, 2009) | Middletown Power, LLC (Owner/Operator) (Started Apr 07, 2009) | DesRoberts, David J (604509) (Started Apr 07, 2009) | Ariagno, Leonard J (646) (Started Nov 20, 2009) |  |  | Operating | Dry bottom wall-fired boiler | Residual Oil | Pipeline Natural Gas |  | Overfire Air |  |  | Electrostatic Precipitator | 1295
8306-01 | NRG | MD2 |  | 95 | 93 |  | 6 | 8306 | 1 | 8306-01 | MD2 |  | Middletown |  | 562 | 2 |  | 2008 |  | 1482 | 12 | 57415 |  | 0.11 | 53.5 | 728969 | EGU |  | 4911 | Electric Services | Middletown Power, LLC (Owner) | NRG Energy, Inc (Operator) | Carpenter, David M (603378) | McFalls, Lee E (1678) |  |  | Operating | Dry bottom wall-fired boiler | Residual Oil | Pipeline Natural Gas |  | Overfire Air |  |  | Electrostatic Precipitator | 1295
8306-02 | NRG | MD3 |  | 96 | 98 | 36 | 6 | 8306 | 2 | 8306-02 | MD3 |  | Middletown |  | 562 | 3 |  | 2010 |  | 1173 | 12 | 151235 |  | 0.19 | 213.4 | 1937944 | EGU |  | 4911 | Electric Services | Middletown Power, LLC (Owner/Operator) | Middletown Power, LLC (Owner/Operator) | DesRoberts, David J (604509) | McFalls, Lee E (1678) (Started Feb 26, 2010) |  |  | Operating | Cyclone boiler | Residual Oil | Pipeline Natural Gas |  | Water Injection | Selective Non-catalytic Reduction |  | Electrostatic Precipitator | 2370
8306-02 | NRG | MD3 |  | 97 | 97 |  | 6 | 8306 | 2 | 8306-02 | MD3 |  | Middletown |  | 562 | 3 |  | 2009 |  | 500 | 12 | 67712 |  | 0.25 | 105.1 | 754650 | EGU |  | 4911 | Electric Services | Middletown Power, LLC (Owner/Operator) (Started Apr 08, 2009) | Middletown Power, LLC (Owner/Operator) (Started Apr 08, 2009) | DesRoberts, David J (604509) (Started Apr 07, 2009) | Ariagno, Leonard J (646) (Started Nov 20, 2009) |  |  | Operating | Cyclone boiler | Residual Oil | Pipeline Natural Gas |  | Water Injection | Selective Non-catalytic Reduction |  | Electrostatic Precipitator | 2370
8306-02 | NRG | MD3 |  | 98 | 96 |  | 6 | 8306 | 2 | 8306-02 | MD3 |  | Middletown |  | 562 | 3 |  | 2008 |  | 626 | 12 | 68834 |  | 0.28 | 149.7 | 908281 | EGU |  | 4911 | Electric Services | Middletown Power, LLC (Owner) | NRG Energy, Inc (Operator) | Carpenter, David M (603378) | McFalls, Lee E (1678) |  |  | Operating | Cyclone boiler | Residual Oil | Pipeline Natural Gas |  | Water Injection | Selective Non-catalytic Reduction |  | Electrostatic Precipitator | 2370
8306-03 | NRG | MD4 |  | 99 | 101 | 37 | 6 | 8306 | 3 | 8306-03 | MD4 |  | Middletown |  | 562 | 4 |  | 2010 |  | 510 | 12 | 59969 |  | 0.16 | 90.5 | 955986 | EGU |  | 4911 | Electric Services | Middletown Power, LLC (Owner) | NRG Energy, Inc (Operator) | DesRoberts, David J (604509) | McFalls, Lee E (1678) (Started Feb 26, 2010) |  |  | Operating | Tangentially-fired | Residual Oil | [6 empty] | 4684
8306-03 | NRG | MD4 |  | 100 | 100 |  | 6 | 8306 | 3 | 8306-03 | MD4 |  | Middletown |  | 562 | 4 |  | 2009 |  | 143 | 12 | 24512 |  | 0.17 | 40.4 | 374322 | EGU |  | 4911 | Electric Services | Middletown Power, LLC (Owner) | NRG Energy, Inc (Operator) | DesRoberts, David J (604509) (Started Apr 07, 2009) | Ariagno, Leonard J (646) (Started Nov 20, 2009) |  |  | Operating | Tangentially-fired | Residual Oil | [6 empty] | 4684
8306-03 | NRG | MD4 |  | 101 | 99 |  | 6 | 8306 | 3 | 8306-03 | MD4 |  | Middletown |  | 562 | 4 |  | 2008 |  | 369 | 12 | 41286 |  | 0.17 | 62.8 | 640297 | EGU |  | 4911 | Electric Services | Middletown Power, LLC (Owner) | NRG Energy, Inc (Operator) | Carpenter, David M (603378) | McFalls, Lee E (1678) |  |  | Operating | Tangentially-fired | Residual Oil | [6 empty] | 4684
#N/A | #N/A | #N/A |  | 102 | 104 | 38 |  | #N/A |  | #N/A | #N/A |  | Milford Power Company LLC |  | 55126 | CT01 |  | 2010 |  | 7931 | 12 | 1939122 |  | 0.02 | 49.7 | 13397425 | EGU |  |  |  | Milford Power Company, LLC (Owner/Operator) | Milford Power Company, LLC (Owner/Operator) | Cartney, Michael E (1384) | Favinger, Thomas G (603710) |  |  | Operating | Combined cycle | Pipeline Natural Gas | Diesel Oil |  | Water Injection | Selective Catalytic Reduction |  |  | 2064
#N/A | #N/A | #N/A |  | 103 | 103 |  |  | #N/A |  | #N/A | #N/A |  | Milford Power Company LLC |  | 55126 | CT01 |  | 2009 |  | 7685 | 12 | 1854472 |  | 0.01 | 45.8 | 12629802 | EGU |  |  |  | Milford Power Company, LLC (Owner/Operator) | Milford Power Company, LLC (Owner/Operator) | Cartney, Michael E (1384) | Favinger, Thomas G (603710) |  |  | Operating | Combined cycle | Pipeline Natural Gas | Diesel Oil |  | Water Injection | Selective Catalytic Reduction |  |  | 2064
#N/A | #N/A | #N/A |  | 104 | 102 |  |  | #N/A |  | #N/A | #N/A |  | Milford Power Company LLC |  | 55126 | CT01 |  | 2008 |  | 5870 | 12 | 1338625 |  | 0.02 | 37 | 9272237 | EGU |  |  |  | Milford Power Company, LLC (Owner/Operator) | Milford Power Company, LLC (Owner/Operator) | Cartney, Michael E (1384) | Favinger, Thomas G (603710) |  |  | Operating | Combined cycle | Pipeline Natural Gas | Diesel Oil |  | Water Injection | Selective Catalytic Reduction |  |  | 2064
#N/A | #N/A | #N/A |  | 105 | 107 | 39 |  | #N/A |  | #N/A | #N/A |  | Milford Power Company LLC |  | 55126 | CT02 |  | 2010 |  | 6309 | 12 | 1539549 |  | 0.02 | 43.7 | 11012521 | EGU |  |  |  | Milford Power Company, LLC (Owner/Operator) | Milford Power Company, LLC (Owner/Operator) | Cartney, Michael E (1384) | Favinger, Thomas G (603710) |  |  | Operating | Combined cycle | Pipeline Natural Gas | Diesel Oil |  | Water Injection | Selective Catalytic Reduction |  |  | 2082
#N/A | #N/A | #N/A |  | 106 | 106 |  |  | #N/A |  | #N/A | #N/A |  | Milford Power Company LLC |  | 55126 | CT02 |  | 2009 |  | 7545 | 12 | 1811093 |  | 0.01 | 48.6 | 12726748 | EGU |  |  |  | Milford Power Company, LLC (Owner/Operator) | Milford Power Company, LLC (Owner/Operator) | Cartney, Michael E (1384) | Favinger, Thomas G (603710) |  |  | Operating | Combined cycle | Pipeline Natural Gas | Diesel Oil |  | Water Injection | Selective Catalytic Reduction |  |  | 2082
#N/A | #N/A | #N/A |  | 107 | 105 |  |  | #N/A |  | #N/A | #N/A |  | Milford Power Company LLC |  | 55126 | CT02 |  | 2008 |  | 6318 | 12 | 1474792 |  | 0.01 | 40.4 | 10414008 | EGU |  |  |  | Milford Power Company, LLC (Owner/Operator) | Milford Power Company, LLC (Owner/Operator) | Cartney, Michael E (1384) | Favinger, Thomas G (603710) |  |  | Operating | Combined cycle | Pipeline Natural Gas | Diesel Oil |  | Water Injection | Selective Catalytic Reduction |  |  | 2082
8306-04 | NRG | MV5 |  | 108 | 110 | 40 | 6 | 8306 | 4 | 8306-04 | MV5 |  | Montville |  | 546 | 5 |  | 2010 |  | 1052 | 12 | 50747 |  | 0.09 | 31.9 | 631690 | EGU |  | 4911 | Electric Services | Montville Power, LLC (Owner/Operator) | Montville Power, LLC (Owner/Operator) | DesRoberts, David J (604509) | McFalls, Lee E (1678) (Started Feb 26, 2010) |  |  | Operating | Tangentially-fired | Residual Oil | Pipeline Natural Gas |  |  |  |  | Electrostatic Precipitator | 995
8300-0 | #N/A | #N/A |  | 109 | 109 |  |  | 8300 |  | 8300-0 | #N/A |  | Montville |  | 546 | 5 |  | 2009 |  | 256 | 12 | 13005 |  | 0.11 | 11.2 | 163032 | EGU |  | 4911 | Electric Services | Montville Power, LLC (Owner/Operator) | Montville Power, LLC (Owner/Operator) | DesRoberts, David J (604509) | Ariagno, Leonard J (646) (Started Nov 20, 2009) |  |  | Operating | Tangentially-fired | Residual Oil | Pipeline Natural Gas |  |  |  |  | Electrostatic Precipitator | 995
8300-0 | #N/A | #N/A |  | 110 | 108 |  |  | 8300 |  | 8300-0 | #N/A |  | Montville |  | 546 | 5 |  | 2008 |  | 444 | 12 | 20012 |  | 0.11 | 15 | 247031 | EGU |  | 4911 | Electric Services | Montville Power, LLC (Owner/Operator) | Montville Power, LLC (Owner/Operator) | DesRoberts, David J (604509) (Started Sep 23, 2008) | McFalls, Lee E (1678) (Started Sep 23, 2008) |  |  | Operating | Tangentially-fired | Residual Oil | Pipeline Natural Gas |  |  |  |  | Electrostatic Precipitator | 995
8306-05 | NRG | MV6 |  | 111 | 113 | 41 | 6 | 8306 | 5 | 8306-05 | MV6 |  | Montville |  | 546 | 6 |  | 2010 |  | 426 | 12 | 45724 |  | 0.14 | 52.1 | 674427 | EGU |  | 4911 | Electric Services | Montville Power, LLC (Owner/Operator) | Montville Power, LLC (Owner/Operator) | DesRoberts, David J (604509) | McFalls, Lee E (1678) (Started Feb 26, 2010) |  |  | Operating | Tangentially-fired | Residual Oil | [6 empty] | 5925
8300-0 | #N/A | #N/A |  | 112 | 112 |  |  | 8300 |  | 8300-0 | #N/A |  | Montville |  | 546 | 6 |  | 2009 |  | 173 | 12 | 21297 |  | 0.17 | 33.4 | 325660 | EGU |  | 4911 | Electric Services | Montville Power, LLC (Owner/Operator) | Montville Power, LLC (Owner/Operator) | DesRoberts, David J (604509) | Ariagno, Leonard J (646) (Started Nov 20, 2009) |  |  | Operating | Tangentially-fired | Residual Oil | [6 empty] | 5925
8300-0 | #N/A | #N/A |  | 113 | 111 |  |  | 8300 |  | 8300-0 | #N/A |  | Montville |  | 546 | 6 |  | 2008 |  | 126 | 12 | 20652 |  | 0.18 | 26.3 | 255457 | EGU |  | 4911 | Electric Services | Montville Power, LLC (Owner/Operator) | Montville Power, LLC (Owner/Operator) | DesRoberts, David J (604509) (Started Sep 23, 2008) | McFalls, Lee E (1678) (Started Sep 23, 2008) |  |  | Operating | Tangentially-fired | Residual Oil | [6 empty] | 5925
8305-01 | PSEG | NHB1 |  | 114 | 116 | 42 |  | 8305 | 1 | 8305-01 | NHB1 |  | New Haven Harbor | 117-0265-TV | 6156 | NHB1 |  | 2010 |  | 1077 | 12 | 168256 |  | 0.13 | 127.5 | 1842328 | EGU |  | 4911 | Electric Services | PSEG (Owner/Operator) | PSEG (Owner/Operator) | Stagliola, Michael (604005) | Strickland, Mark F (603622) |  |  | Operating | Tangentially-fired | Residual Oil | Diesel Oil, Pipeline Natural Gas |  |  |  |  | Electrostatic Precipitator | 4425
8305-01 | PSEG | NHB1 |  | 115 | 115 |  |  | 8305 | 1 | 8305-01 | NHB1 |  | New Haven Harbor | 117-0265-TV | 6156 | NHB1 |  | 2009 |  | 703 | 12 | 152988 |  | 0.13 | 115.4 | 1640110 | EGU |  | 4911 | Electric Services | PSEG (Owner/Operator) | PSEG (Owner/Operator) | Stagliola, Michael (604005) (Started Oct 09, 2009) | Strickland, Mark F (603622) |  |  | Operating | Tangentially-fired | Residual Oil | Diesel Oil, Pipeline Natural Gas |  |  |  |  | Electrostatic Precipitator | 4425
8305-01 | PSEG | NHB1 |  | 116 | 114 |  |  | 8305 | 1 | 8305-01 | NHB1 |  | New Haven Harbor | 117-0265-TV | 6156 | NHB1 |  | 2008 |  | 839 | 12 | 138007 |  | 0.14 | 117.8 | 1570919 | EGU |  | 4911 | Electric Services | PSEG (Owner/Operator) | PSEG (Owner/Operator) | Packer, Larry (603648) | Strickland, Mark F (603622) |  |  | Operating | Tangentially-fired | Residual Oil | Diesel Oil, Pipeline Natural Gas |  |  |  |  | Electrostatic Precipitator | 4425
8306-06 | NRG | NH1 |  | 117 | 119 | 43 | 6 | 8306 | 6 | 8306-06 | NH1 |  | Norwalk Harbor Station |  | 548 | 1 | CS0001 | 2010 |  | 885 | 12 | 38314 |  | 0.13 | 36.4 | 447264 | EGU |  | 4911 | Electric Services | Norwalk Power, LLC (Owner/Operator) | Norwalk Power, LLC (Owner/Operator) | Ross, Leslie E (1680) | DesRoberts, David J (604509) |  |  | Operating | Tangentially-fired | Residual Oil |  |  | Selective Non-catalytic Reduction |  |  | Electrostatic Precipitator | 1776
8300-06 | NRG | CC14 |  | 118 | 118 |  |  | 8300 | 6 | 8300-06 | CC14 |  | Norwalk Harbor Station |  | 548 | 1 | CS0001 | 2009 |  | 304 | 12 | 16636 |  | 0.11 | 17.4 | 201785 | EGU |  | 4911 | Electric Services | Norwalk Power, LLC (Owner/Operator) | Norwalk Power, LLC (Owner/Operator) | Ross, Leslie E (1680) | DesRoberts, David J (604509) (Started Dec 28, 2009) |  |  | Operating | Tangentially-fired | Residual Oil |  |  | Selective Non-catalytic Reduction |  |  | Electrostatic Precipitator | 1776
8300-06 | NRG | CC14 |  | 119 | 117 |  |  | 8300 | 6 | 8300-06 | CC14 |  | Norwalk Harbor Station |  | 548 | 1 | CS0001 | 2008 |  | 1604 | 12 | 90980 |  | 0.14 | 95.6 | 1180412 | EGU |  | 4911 | Electric Services | Norwalk Power, LLC (Owner/Operator) | Norwalk Power, LLC (Owner/Operator) | Ross, Leslie E (1680) | McFalls, Lee E (1678) (Started May 06, 2008) |  |  | Operating | Tangentially-fired | Residual Oil |  |  | Selective Non-catalytic Reduction |  |  | Electrostatic Precipitator | 1776
8300-10 | NRG | NH10 |  | 120 | 122 | 44 |  | 8300 | 10 | 8300-10 | NH10 |  | Norwalk Harbor Station |  | 548 | 10 |  | 2010 |  | 22 | 6 | 216 |  | 1.17 | 0 | 13 | EGU |  | 4911 | Electric Services | Norwalk Power, LLC (Owner/Operator) | Norwalk Power, LLC (Owner/Operator) | Ross, Leslie E (1680) | DesRoberts, David J (604509) |  |  | Operating | Other turbine | Other Oil | [6 empty] | 232
8300-0 | #N/A | #N/A |  | 121 | 121 |  |  | 8300 |  | 8300-0 | #N/A |  | Norwalk Harbor Station |  | 548 | 10 |  | 2009 |  | 6 | 6 | 55 |  | 1.17 | 0 | 4 | EGU |  | 4911 | Electric Services | Norwalk Power, LLC (Owner/Operator) | Norwalk Power, LLC (Owner/Operator) | Ross, Leslie E (1680) | DesRoberts, David J (604509) (Started Dec 28, 2009) |  |  | Operating | Other turbine | Other Oil | [6 empty] | 232
8300-0 | #N/A | #N/A |  | 122 | 120 |  |  | 8300 |  | 8300-0 | #N/A |  | Norwalk Harbor Station |  | 548 | 10 |  | 2008 |  | 8 | 6 | 67 |  | 1.18 | 0.3 | 468 | EGU |  | 4911 | Electric Services | Norwalk Power, LLC (Owner/Operator) | Norwalk Power, LLC (Owner/Operator) | Ross, Leslie E (1680) | McFalls, Lee E (1678) (Started May 06, 2008) |  |  | Operating | Other turbine | Other Oil | [6 empty] | 232
8306-07 | NRG | NH2 |  | 123 | 125 | 45 | 6 | 8306 | 7 | 8306-07 | NH2 |  | Norwalk Harbor Station |  | 548 | 2 | CS0001 | 2010 |  | 928 | 12 | 45429 |  | 0.13 | 43.9 | 533193 | EGU |  | 4911 | Electric Services | Norwalk Power, LLC (Owner/Operator) | Norwalk Power, LLC (Owner/Operator) | Ross, Leslie E (1680) | DesRoberts, David J (604509) |  |  | Operating | Tangentially-fired | Residual Oil |  |  | Selective Non-catalytic Reduction |  |  | Electrostatic Precipitator | 1776
8300-07 | NRG | FD10 |  | 124 | 124 |  |  | 8300 | 7 | 8300-07 | FD10 |  | Norwalk Harbor Station |  | 548 | 2 | CS0001 | 2009 |  | 458 | 12 | 23327 |  | 0.12 | 22.7 | 292868 | EGU |  | 4911 | Electric Services | Norwalk Power, LLC (Owner/Operator) | Norwalk Power, LLC (Owner/Operator) | Ross, Leslie E (1680) | DesRoberts, David J (604509) (Started Dec 28, 2009) |  |  | Operating | Tangentially-fired | Residual Oil |  |  | Selective Non-catalytic Reduction |  |  | Electrostatic Precipitator | 1776
8300-07 | NRG | FD10 |  | 125 | 123 |  |  | 8300 | 7 | 8300-07 | FD10 |  | Norwalk Harbor Station |  | 548 | 2 | CS0001 | 2008 |  | 2981 | 12 | 151100 |  | 0.13 | 160.4 | 2033661 | EGU |  | 4911 | Electric Services | Norwalk Power, LLC (Owner/Operator) | Norwalk Power, LLC (Owner/Operator) | Ross, Leslie E (1680) | McFalls, Lee E (1678) (Started May 06, 2008) |  |  | Operating | Tangentially-fired | Residual Oil |  |  | Selective Non-catalytic Reduction |  |  | Electrostatic Precipitator | 1776
8304-01 | NPU | TRBINE |  | 126 | 128 | 46 |  | 8304 | 1 | 8304-01 | TRBINE |  | Norwich |  | 581 | TRBINE |  | 2010 |  | 19 | 6 | 327 |  | 0.62 | 1.5 | 4811 | EGU |  | 4911 | Electric Services | Norwich Public Utilities (Owner/Operator) | Norwich Public Utilities (Owner/Operator) | LaRose, Christopher (2835) | Greene, Mark (601662) |  |  | Operating | Combustion turbine | Diesel Oil | [6 empty] | 249
8304-01 | NPU | TRBINE |  | 127 | 127 |  |  | 8304 | 1 | 8304-01 | TRBINE |  | Norwich |  | 581 | TRBINE |  | 2009 |  | 15 | 6 | 225 |  | 0.62 | 1.2 | 3782 | EGU |  | 4911 | Electric Services | Norwich Public Utilities (Owner/Operator) | Norwich Public Utilities (Owner/Operator) | LaRose, Christopher (2835) | Greene, Mark (601662) |  |  | Operating | Combustion turbine | Diesel Oil | [6 empty] | 249
8304-01 | NPU | TRBINE |  | 128 | 126 |  |  | 8304 | 1 | 8304-01 | TRBINE |  | Norwich |  | 581 | TRBINE |  | 2008 |  | 10 | 6 | 151 |  | 0.57 | 0.7 | 2595 | EGU |  | 4911 | Electric Services | Norwich Public Utilities (Owner/Operator) | Norwich Public Utilities (Owner/Operator) | LaRose, Christopher (2835) (Started Oct 24, 2008) | Greene, Mark (601662) (Started Oct 24, 2008) |  |  | Operating | Combustion turbine | Diesel Oil | [6 empty] | 249
#N/A | #N/A | #N/A |  | 129 | 131 | 47 |  | #N/A |  | #N/A | #N/A |  | Pfizer |  | 54236 | 5 |  | 2010 |  | 2565 | 12 |  | 289584 | 0.12 | 22 | 350918 | NON EGU |  | 2834 | Pharmaceutical Preparations | Pfizer, Inc. (Owner/Operator) | Pfizer, Inc. (Owner/Operator) | Smith, Scott W (602520) | O'Connor, Steven J (603966) |  |  | Operating | Dry bottom wall-fired boiler | Residual Oil | Pipeline Natural Gas | [5 empty] | 501.6
#N/A | #N/A | #N/A |  | 130 | 130 |  |  | #N/A |  | #N/A | #N/A |  | Pfizer |  | 54236 | 5 |  | 2009 |  | 4458 | 12 |  | 539830 | 0.19 | 59.6 | 616500 | NON EGU |  | 2834 | Pharmaceutical Preparations | Pfizer, Inc. (Owner/Operator) | Pfizer, Inc. (Owner/Operator) | Smith, Scott W (602520) | O'Connor, Steven J (603966) |  |  | Operating | Dry bottom wall-fired boiler | Residual Oil | Pipeline Natural Gas | [5 empty] | 501.6
#N/A | #N/A | #N/A |  | 131 | 129 |  |  | #N/A |  | #N/A | #N/A |  | Pfizer |  | 54236 | 5 |  | 2008 |  | 2230 | 12 |  | 297220 | 0.12 | 25.2 | 385960 | NON EGU |  | 2834 | Pharmaceutical Preparations | Pfizer, Inc. (Owner/Operator) | Pfizer, Inc. (Owner/Operator) | Smith, Scott W (602520) | O'Connor, Steven J (603966) (Started Feb 11, 2008) |  |  | Operating | Dry bottom wall-fired boiler | Residual Oil | Pipeline Natural Gas | [5 empty] | 501.6
#N/A | #N/A | #N/A |  | 132 | 132 | 48 |  | #N/A |  | #N/A | #N/A |  | Pfizer |  | 54236 | 8 |  | 2008 |  | 1363 | 9 |  | 159356 | 0.11 | 10.9 | 191787 | NON EGU |  | 2834 | Pharmaceutical Preparations | Pfizer, Inc. (Owner/Operator) | Pfizer, Inc. (Owner/Operator) | Smith, Scott W (602520) | O'Connor, Steven J (603966) (Started Feb 11, 2008) |  |  | Operating (Retired 09/30/2008) | Dry bottom wall-fired boiler | Residual Oil | Pipeline Natural Gas | [5 empty] | 266
#N/A | #N/A | #N/A |  | 133 | 135 | 49 |  | #N/A |  | #N/A | #N/A |  | Pratt & Whitney, East Hartford |  | 54605 | 001 |  | 2010 |  | 5844 | 12 | 145703 |  | 0.02 | 17.6 | 1564973 | NON EGU |  | 3511 | Turbines and Turbine Generator | P&W, Division of United Technologies (Owner/Operator) | P&W, Division of United Technologies (Owner/Operator) | Russell, David M (602966) | Wyman, Kip (601544) |  |  | Operating | Combustion turbine | Pipeline Natural Gas | Diesel Oil |  | Water Injection | Selective Catalytic Reduction |  |  | 365.7
#N/A | #N/A | #N/A |  | 134 | 134 |  |  | #N/A |  | #N/A | #N/A |  | Pratt & Whitney, East Hartford |  | 54605 | 001 |  | 2009 |  | 5531 | 12 | 135676 |  | 0.02 | 16.3 | 1462909 | NON EGU |  | 3511 | Turbines and Turbine Generator | P&W, Division of United Technologies (Owner/Operator) | P&W, Division of United Technologies (Owner/Operator) | Russell, David M (602966) | Wyman, Kip (601544) (Started May 28, 2009) |  |  | Operating | Combustion turbine | Pipeline Natural Gas | Diesel Oil |  | Water Injection | Selective Catalytic Reduction |  |  | 365.7
#N/A | #N/A | #N/A |  | 135 | 133 |  |  | #N/A |  | #N/A | #N/A |  | Pratt & Whitney, East Hartford |  | 54605 | 001 |  | 2008 |  | 6188 | 12 | 147147 |  | 0.02 | 18.5 | 1622357 | NON EGU |  | 3511 | Turbines and Turbine Generator | P&W, Division of United Technologies (Owner/Operator) | P&W, Division of United Technologies (Owner/Operator) | Russell, David M (602966) | Quattrocchi, Louis (604242) (Started Jul 23, 2008) |  |  | Operating | Combustion turbine | Pipeline Natural Gas | Diesel Oil |  | Water Injection | Selective Catalytic Reduction |  |  | 365.7
8302-01 | CRRA | 11A |  | 136 | 138 | 50 |  | 8302 | 1 | 8302-01 | 11A |  | South Meadow Station | 075-0252-TV | 563 | 11A |  | 2010 |  | 23 | 12 | 298 |  | 0.75 | 1.5 | 3882 | EGU |  | 4911 | Electric Services | Connecticut Resources Recovery (Owner/Operator) | Connecticut Resources Recovery (Owner/Operator) | Egan, Peter (2263) | Yates, Steven (2264) |  |  | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-01 | CRRA | 11A |  | 137 | 137 |  |  | 8302 | 1 | 8302-01 | 11A |  | South Meadow Station | 075-0252-TV | 563 | 11A |  | 2009 |  | 22 | 12 | 264 |  | 0.8 | 1.4 | 3368 | EGU |  | 4911 | Electric Services | Connecticut Resources Recovery (Owner/Operator) | Connecticut Resources Recovery (Owner/Operator) | Egan, Peter (2263) | Yates, Steven (2264) |  |  | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-01 | CRRA | 11A |  | 138 | 136 |  |  | 8302 | 1 | 8302-01 | 11A |  | South Meadow Station | 075-0252-TV | 563 | 11A |  | 2008 |  | 12 | 6 | 126 |  | 0.83 | 0.7 | 1575 | EGU |  | 4911 | Electric Services | Connecticut Resources Recovery (Owner/Operator) | Connecticut Resources Recovery (Owner/Operator) | Egan, Peter (2263) | Yates, Steven (2264) |  |  | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-02 | CRRA | 11B |  | 139 | 141 | 51 |  | 8302 | 2 | 8302-02 | 11B |  | South Meadow Station | 075-0252-TV | 563 | 11B |  | 2010 |  | 23 | 12 | 298 |  | 0.76 | 1.5 | 3882 | EGU |  | 4911 | Electric Services | Connecticut Resources Recovery (Owner/Operator) | Connecticut Resources Recovery (Owner/Operator) | Egan, Peter (2263) | Yates, Steven (2264) |  |  | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-02 | 0 | 11B |  | 140 | 140 |  |  | 8302 | 2 | 8302-02 | 11B |  | South Meadow Station | 075-0252-TV | 563 | 11B |  | 2009 |  | 22 | 12 | 264 |  | 0.73 | 1.2 | 3368 | EGU |  | 4911 | Electric Services | Connecticut Resources Recovery (Owner/Operator) | Connecticut Resources Recovery (Owner/Operator) | Egan, Peter (2263) | Yates, Steven (2264) |  |  | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-02 | 0 | 11B |  | 141 | 139 |  |  | 8302 | 2 | 8302-02 | 11B |  | South Meadow Station | 075-0252-TV | 563 | 11B |  | 2008 |  | 12 | 6 | 126 |  | 0.73 | 0.6 | 1575 | EGU |  | 4911 | Electric Services | Connecticut Resources Recovery (Owner/Operator) | Connecticut Resources Recovery (Owner/Operator) | Egan, Peter (2263) | Yates, Steven (2264) |  |  | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-03 | CRRA | 12A |  | 142 | 144 | 52 |  | 8302 | 3 | 8302-03 | 12A |  | South Meadow Station | 075-0252-TV | 563 | 12A |  | 2010 |  | 26 | 12 | 361 |  | 0.8 | 1.9 | 4770 | EGU |  | 4911 | Electric Services | Connecticut Resources Recovery (Owner/Operator) | Connecticut Resources Recovery (Owner/Operator) | Egan, Peter (2263) | Yates, Steven (2264) |  |  | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-03 | 0 | 12A |  | 143 | 143 |  |  | 8302 | 3 | 8302-03 | 12A |  | South Meadow Station | 075-0252-TV | 563 | 12A |  | 2009 |  | 21 | 12 | 272 |  | 0.8 | 1.4 | 3507 | EGU |  | 4911 | Electric Services | Connecticut Resources Recovery (Owner/Operator) | Connecticut Resources Recovery (Owner/Operator) | Egan, Peter (2263) | Yates, Steven (2264) |  |  | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-03 | 0 | 12A |  | 144 | 142 |  |  | 8302 | 3 | 8302-03 | 12A |  | South Meadow Station | 075-0252-TV | 563 | 12A |  | 2008 |  | 11 | 6 | 123 |  | 0.8 | 0.6 | 1560 | EGU |  | 4911 | Electric Services | Connecticut Resources Recovery (Owner/Operator) | Connecticut Resources Recovery (Owner/Operator) | Egan, Peter (2263) | Yates, Steven (2264) |  |  | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-04 | CRRA | 12B |  | 145 | 147 | 53 |  | 8302 | 4 | 8302-04 | 12B |  | South Meadow Station | 075-0252-TV | 563 | 12B |  | 2010 |  | 26 | 12 | 361 |  | 0.76 | 1.8 | 4770 | EGU |  | 4911 | Electric Services | Connecticut Resources Recovery (Owner/Operator) | Connecticut Resources Recovery (Owner/Operator) | Egan, Peter (2263) | Yates, Steven (2264) |  |  | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-04 | 0 | 12B |  | 146 | 146 |  |  | 8302 | 4 | 8302-04 | 12B |  | South Meadow Station | 075-0252-TV | 563 | 12B |  | 2009 |  | 21 | 12 | 272 |  | 0.73 | 1.3 | 3507 | EGU |  | 4911 | Electric Services | Connecticut Resources Recovery (Owner/Operator) | Connecticut Resources Recovery (Owner/Operator) | Egan, Peter (2263) | Yates, Steven (2264) |  |  | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-04 | 0 | 12B |  | 147 | 145 |  |  | 8302 | 4 | 8302-04 | 12B |  | South Meadow Station | 075-0252-TV | 563 | 12B |  | 2008 |  | 11 | 6 | 123 |  | 0.72 | 0.6 | 1560 | EGU |  | 4911 | Electric Services | Connecticut Resources Recovery (Owner/Operator) | Connecticut Resources Recovery (Owner/Operator) | Egan, Peter (2263) | Yates, Steven (2264) |  |  | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-05 | CRRA | 13A |  | 148 | 150 | 54 |  | 8302 | 5 | 8302-05 | 13A |  | South Meadow Station | 075-0252-TV | 563 | 13A |  | 2010 |  | 25 | 12 | 326 |  | 0.81 | 1.8 | 4308 | EGU |  | 4911 | Electric Services | Connecticut Resources Recovery (Owner/Operator) | Connecticut Resources Recovery (Owner/Operator) | Egan, Peter (2263) | Yates, Steven (2264) |  |  | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-05 | 0 | 13A |  | 149 | 149 |  |  | 8302 | 5 | 8302-05 | 13A |  | South Meadow Station | 075-0252-TV | 563 | 13A |  | 2009 |  | 24 | 12 | 284 |  | 0.82 | 1.5 | 3611 | EGU |  | 4911 | Electric Services | Connecticut Resources Recovery (Owner/Operator) | Connecticut Resources Recovery (Owner/Operator) | Egan, Peter (2263) | Yates, Steven (2264) |  |  | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-05 | 0 | 13A |  | 150 | 148 |  |  | 8302 | 5 | 8302-05 | 13A |  | South Meadow Station | 075-0252-TV | 563 | 13A |  | 2008 |  | 12 | 6 | 111 |  | 0.88 | 0.6 | 1405 | EGU |  | 4911 | Electric Services | Connecticut Resources Recovery (Owner/Operator) | Connecticut Resources Recovery (Owner/Operator) | Egan, Peter (2263) | Yates, Steven (2264) |  |  | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-06 | CRRA | 13B |  | 151 | 153 | 55 |  | 8302 | 6 | 8302-06 | 13B |  | South Meadow Station | 075-0252-TV | 563 | 13B |  | 2010 |  | 25 | 12 | 326 |  | 0.79 | 1.7 | 4308 | EGU |  | 4911 | Electric Services | Connecticut Resources Recovery (Owner/Operator) | Connecticut Resources Recovery (Owner/Operator) | Egan, Peter (2263) | Yates, Steven (2264) |  |  | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-06 | 0 | 13B |  | 152 | 152 |  |  | 8302 | 6 | 8302-06 | 13B |  | South Meadow Station | 075-0252-TV | 563 | 13B |  | 2009 |  | 24 | 12 | 284 |  | 0.79 | 1.4 | 3611 | EGU |  | 4911 | Electric Services | Connecticut Resources Recovery (Owner/Operator) | Connecticut Resources Recovery (Owner/Operator) | Egan, Peter (2263) | Yates, Steven (2264) |  |  | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-06 | 0 | 13B |  | 153 | 151 |  |  | 8302 | 6 | 8302-06 | 13B |  | South Meadow Station | 075-0252-TV | 563 | 13B |  | 2008 |  | 12 | 6 | 111 |  | 0.84 | 0.6 | 1405 | EGU |  | 4911 | Electric Services | Connecticut Resources Recovery (Owner/Operator) | Connecticut Resources Recovery (Owner/Operator) | Egan, Peter (2263) | Yates, Steven (2264) |  |  | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-07 | CRRA | 14A |  | 154 | 156 | 56 |  | 8302 | 7 | 8302-07 | 14A |  | South Meadow Station | 075-0252-TV | 563 | 14A |  | 2010 |  | 24 | 12 | 296 |  | 0.82 | 1.6 | 3909 | EGU |  | 4911 | Electric Services | Connecticut Resources Recovery (Owner/Operator) | Connecticut Resources Recovery (Owner/Operator) | Egan, Peter (2263) | Yates, Steven (2264) |  |  | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-07 | 0 | 14A |  | 155 | 155 |  |  | 8302 | 7 | 8302-07 | 14A |  | South Meadow Station | 075-0252-TV | 563 | 14A |  | 2009 |  | 19 | 12 | 239 |  | 0.82 | 1.3 | 3094 | EGU |  | 4911 | Electric Services | Connecticut Resources Recovery (Owner/Operator) | Connecticut Resources Recovery (Owner/Operator) | Egan, Peter (2263) | Yates, Steven (2264) |  |  | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-07 | 0 | 14A |  | 156 | 154 |  |  | 8302 | 7 | 8302-07 | 14A |  | South Meadow Station | 075-0252-TV | 563 | 14A |  | 2008 |  | 9 | 6 | 89 |  | 0.87 | 0.5 | 1135 | EGU |  | 4911 | Electric Services | Connecticut Resources Recovery (Owner/Operator) | Connecticut Resources Recovery (Owner/Operator) | Egan, Peter (2263) | Yates, Steven (2264) |  |  | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-08 | CRRA | 14B |  | 157 | 159 | 57 |  | 8302 | 8 | 8302-08 | 14B |  | South Meadow Station | 075-0252-TV | 563 | 14B |  | 2010 |  | 24 | 12 | 296 |  | 0.83 | 1.7 | 3909 | EGU |  | 4911 | Electric Services | Connecticut Resources Recovery (Owner/Operator) | Connecticut Resources Recovery (Owner/Operator) | Egan, Peter (2263) | Yates, Steven (2264) |  |  | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-08 | 0 | 14B |  | 158 | 158 |  |  | 8302 | 8 | 8302-08 | 14B |  | South Meadow Station | 075-0252-TV | 563 | 14B |  | 2009 |  | 19 | 12 | 239 |  | 0.75 | 1.2 | 3094 | EGU |  | 4911 | Electric Services | Connecticut Resources Recovery (Owner/Operator) | Connecticut Resources Recovery (Owner/Operator) | Egan, Peter (2263) | Yates, Steven (2264) |  |  | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8302-08 | 0 | 14B |  | 159 | 157 |  |  | 8302 | 8 | 8302-08 | 14B |  | South Meadow Station | 075-0252-TV | 563 | 14B |  | 2008 |  | 9 | 6 | 89 |  | 0.74 | 0.4 | 1135 | EGU |  | 4911 | Electric Services | Connecticut Resources Recovery (Owner/Operator) | Connecticut Resources Recovery (Owner/Operator) | Egan, Peter (2263) | Yates, Steven (2264) |  |  | Operating | Combustion turbine | Diesel Oil | [6 empty] | 266
8300-08 | NRG | TT10 |  | 160 | 162 | 58 |  | 8300 | 8 | 8300-08 | TT10 |  | Torrington Terminal |  | 565 | 10 |  | 2010 |  | 36 | 6 | 468 |  | 1.2 | 5.4 | 9070 | EGU |  | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) | Connecticut Jet Power, LLC (Owner/Operator) | Ross, Leslie E (1680) | DesRoberts, David J (604509) |  |  | Operating | Combustion turbine | Other Oil | [6 empty] | 250
8300-08 | NRG | TT10 |  | 161 | 161 |  |  | 8300 | 8 | 8300-08 | TT10 |  | Torrington Terminal |  | 565 | 10 |  | 2009 |  | 6 | 6 | 91 |  | 1.2 | 0.8 | 1408 | EGU |  | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) | Connecticut Jet Power, LLC (Owner/Operator) | Ross, Leslie E (1680) (Started Dec 28, 2009) | DesRoberts, David J (604509) (Started Dec 28, 2009) |  |  | Operating | Combustion turbine | Other Oil | [6 empty] | 250
8300-08 | NRG | TT10 |  | 162 | 160 |  |  | 8300 | 8 | 8300-08 | TT10 |  | Torrington Terminal |  | 565 | 10 |  | 2008 |  | 6 | 6 | 111 |  | 1.2 | 0.9 | 1450 | EGU |  | 4911 | Electric Services | Connecticut Jet Power, LLC (Owner/Operator) | Connecticut Jet Power, LLC (Owner/Operator) | Carpenter, David M (603378) (Started Nov 17, 2008) | McFalls, Lee E (1678) (Started Nov 17, 2008) |  |  | Operating | Combustion turbine | Other Oil | [6 empty] | 250
8303-01 | FirstLight | 10 |  | 163 | 165 | 59 |  | 8303 | 1 | 8303-01 | 10 |  | Tunnel |  | 557 | 10 |  | 2010 |  | 20 | 6 | 301 |  | 0.73 | 1.7 | 4575 | EGU |  | 4911 | Electric Services | FirstLight Hydro Generating Company (Owner) (Started Oct 19, 2010) | FirstLight Power Resources (Operator) | Donohue, James P (603193) | Padberg, Thomas (602103) (Started Oct 19, 2010) |  |  | Operating | Combustion turbine | Diesel Oil | [6 empty] | 243
8303-01 | FirstLight | 10 |  | 164 | 164 |  |  | 8303 | 1 | 8303-01 | 10 |  | Tunnel |  | 557 | 10 |  | 2009 |  | 3 | 6 | 46 |  | 0.79 | 0.3 | 808 | EGU |  | 4911 | Electric Services | FirstLight Power Resources (Owner/Operator) | FirstLight Power Resources (Owner/Operator) | Donohue, James P (603193) (Started Mar 12, 2009) | Vodopivec, Cynthia (603383) (Started Mar 12, 2009) |  |  | Operating | Combustion turbine | Diesel Oil | [6 empty] | 243
8303-01 | FirstLight | 10 |  | 165 | 163 |  |  | 8303 | 1 | 8303-01 | 10 |  | Tunnel |  | 557 | 10 |  | 2008 |  | 15 | 6 | 153 |  | 0.74 | 1 | 2596 | EGU |  | 4911 | Electric Services | FirstLight Power Resources (Owner/Operator) | FirstLight Power Resources (Owner/Operator) | Campbell, John P (603412) | Donohue, James P (603193) |  |  | Operating | Combustion turbine | Diesel Oil | [6 empty] | 243
#N/A | #N/A | #N/A |  | 166 | 168 | 60 |  | #N/A |  | #N/A | #N/A |  | Wallingford Energy, LLC |  | 55517 | CT01 |  | 2010 |  | 1183 | 12 | 51592 |  | 0.02 | 2.7 | 510800 | EGU |  | 4911 | Electric Services | PPL Wallingford Energy, LLC (Owner/Operator) | PPL Wallingford Energy, LLC (Owner/Operator) | Murphy, Dennis J (1700) | Boyer, Linda A (500568) |  |  | Operating | Combustion turbine | Pipeline Natural Gas |  |  | Water Injection | Selective Catalytic Reduction |  |  | 530
#N/A | #N/A | #N/A |  | 167 | 167 |  |  | #N/A |  | #N/A | #N/A |  | Wallingford Energy, LLC |  | 55517 | CT01 |  | 2009 |  | 597 | 12 | 26677 |  | 0.02 | 1.6 | 260885 | EGU |  | 4911 | Electric Services | PPL Wallingford Energy, LLC (Owner/Operator) | PPL Wallingford Energy, LLC (Owner/Operator) | Murphy, Dennis J (1700) | Boyer, Linda A (500568) (Started Apr 09, 2009) |  |  | Operating | Combustion turbine | Pipeline Natural Gas |  |  | Water Injection | Selective Catalytic Reduction |  |  | 530
#N/A | #N/A | #N/A |  | 168 | 166 |  |  | #N/A |  | #N/A | #N/A |  | Wallingford Energy, LLC |  | 55517 | CT01 |  | 2008 |  | 779 | 12 | 34539 |  | 0.02 | 1.9 | 334474 | EGU |  | 4911 | Electric Services | PPL Wallingford Energy, LLC (Owner/Operator) | PPL Wallingford Energy, LLC (Owner/Operator) | Murphy, Dennis J (1700) (Started Feb 20, 2008) |  |  |  | Operating | Combustion turbine | Pipeline Natural Gas |  |  | Water Injection | Selective Catalytic Reduction |  |  | 530
#N/A | #N/A | #N/A |  | 169 | 171 | 61 |  | #N/A |  | #N/A | #N/A |  | Wallingford Energy, LLC |  | 55517 | CT02 |  | 2010 |  | 1155 | 12 | 49283 |  | 0.01 | 2.3 | 461536 | EGU |  | 4911 | Electric Services | PPL Wallingford Energy, LLC (Owner/Operator) | PPL Wallingford Energy, LLC (Owner/Operator) | Murphy, Dennis J (1700) | Boyer, Linda A (500568) |  |  | Operating | Combustion turbine | Pipeline Natural Gas |  |  | Water Injection | Selective Catalytic Reduction |  |  | 530
#N/A | #N/A | #N/A |  | 170 | 170 |  |  | #N/A |  | #N/A | #N/A |  | Wallingford Energy, LLC |  | 55517 | CT02 |  | 2009 |  | 516 | 12 | 16821 |  | 0.02 | 1.3 | 218469 | EGU |  | 4911 | Electric Services | PPL Wallingford Energy, LLC (Owner/Operator) | PPL Wallingford Energy, LLC (Owner/Operator) | Murphy, Dennis J (1700) | Boyer, Linda A (500568) (Started Apr 09, 2009) |  |  | Operating | Combustion turbine | Pipeline Natural Gas |  |  | Water Injection | Selective Catalytic Reduction |  |  | 530
#N/A | #N/A | #N/A |  | 171 | 169 |  |  | #N/A |  | #N/A | #N/A |  | Wallingford Energy, LLC |  | 55517 | CT02 |  | 2008 |  | 725 | 12 | 31778 |  | 0.01 | 1.5 | 305552 | EGU |  | 4911 | Electric Services | PPL Wallingford Energy, LLC (Owner/Operator) | PPL Wallingford Energy, LLC (Owner/Operator) | Murphy, Dennis J (1700) (Started Feb 20, 2008) |  |  |  | Operating | Combustion turbine | Pipeline Natural Gas |  |  | Water Injection | Selective Catalytic Reduction |  |  | 530
#N/A | #N/A | #N/A |  | 172 | 174 | 62 |  | #N/A |  | #N/A | #N/A |  | Wallingford Energy, LLC |  | 55517 | CT03 |  | 2010 |  | 915 | 12 | 40261 |  | 0.02 | 2.3 | 388303 | EGU |  | 4911 | Electric Services | PPL Wallingford Energy, LLC (Owner/Operator) | PPL Wallingford Energy, LLC (Owner/Operator) | Murphy, Dennis J (1700) | Boyer, Linda A (500568) |  |  | Operating | Combustion turbine | Pipeline Natural Gas |  |  | Water Injection | Selective Catalytic Reduction |  |  | 530
#N/A | #N/A | #N/A |  | 173 | 173 |  |  | #N/A |  | #N/A | #N/A |  | Wallingford Energy, LLC |  | 55517 | CT03 |  | 2009 |  | 375 | 12 | 16753 |  | 0.02 | 1.2 | 157014 | EGU |  | 4911 | Electric Services | PPL Wallingford Energy, LLC (Owner/Operator) | PPL Wallingford Energy, LLC (Owner/Operator) | Murphy, Dennis J (1700) | Boyer, Linda A (500568) (Started Apr 09, 2009) |  |  | Operating | Combustion turbine | Pipeline Natural Gas |  |  | Water Injection | Selective Catalytic Reduction |  |  | 530
#N/A | #N/A | #N/A |  | 174 | 172 |  |  | #N/A |  | #N/A | #N/A |  | Wallingford Energy, LLC |  | 55517 | CT03 |  | 2008 |  | 417 | 12 | 18147 |  | 0.03 | 1.2 | 174401 | EGU |  | 4911 | Electric Services | PPL Wallingford Energy, LLC (Owner/Operator) | PPL Wallingford Energy, LLC (Owner/Operator) | Murphy, Dennis J (1700) (Started Feb 20, 2008) |  |  |  | Operating | Combustion turbine | Pipeline Natural Gas |  |  | Water Injection | Selective Catalytic Reduction |  |  | 530
#N/A | #N/A | #N/A |  | 175 | 177 | 63 |  | #N/A |  | #N/A | #N/A |  | Wallingford Energy, LLC |  | 55517 | CT04 |  | 2010 |  | 982 | 12 | 43026 |  | 0.01 | 2.2 | 422264 | EGU |  | 4911 | Electric Services | PPL Wallingford Energy, LLC (Owner/Operator) | PPL Wallingford Energy, LLC (Owner/Operator) | Murphy, Dennis J (1700) | Boyer, Linda A (500568) |  |  | Operating | Combustion turbine | Pipeline Natural Gas |  |  | Water Injection | Selective Catalytic Reduction |  |  | 530
#N/A | #N/A | #N/A |  | 176 | 176 |  |  | #N/A |  | #N/A | #N/A |  | Wallingford Energy, LLC |  | 55517 | CT04 |  | 2009 |  | 630 | 12 | 27997 |  | 0.02 | 1.4 | 257370 | EGU |  | 4911 | Electric Services | PPL Wallingford Energy, LLC (Owner/Operator) | PPL Wallingford Energy, LLC (Owner/Operator) | Murphy, Dennis J (1700) | Boyer, Linda A (500568) (Started Apr 09, 2009) |  |  | Operating | Combustion turbine | Pipeline Natural Gas |  |  | Water Injection | Selective Catalytic Reduction |  |  | 530
#N/A | #N/A | #N/A |  | 177 | 175 |  |  | #N/A |  | #N/A | #N/A |  | Wallingford Energy, LLC |  | 55517 | CT04 |  | 2008 |  | 638 | 12 | 27926 |  | 0.02 | 1.7 | 273789 | EGU |  | 4911 | Electric Services | PPL Wallingford Energy, LLC (Owner/Operator) | PPL Wallingford Energy, LLC (Owner/Operator) | Murphy, Dennis J (1700) (Started Feb 20, 2008) |  |  |  | Operating | Combustion turbine | Pipeline Natural Gas |  |  | Water Injection | Selective Catalytic Reduction |  |  | 530
#N/A | #N/A | #N/A |  | 178 | 180 | 64 |  | #N/A |  | #N/A | #N/A |  | Wallingford Energy, LLC |  | 55517 | CT05 |  | 2010 |  | 964 | 12 | 42889 |  | 0.01 | 2 | 409124 | EGU |  | 4911 | Electric Services | PPL Wallingford Energy, LLC (Owner/Operator) | PPL Wallingford Energy, LLC (Owner/Operator) | Murphy, Dennis J (1700) | Boyer, Linda A (500568) |  |  | Operating | Combustion turbine | Pipeline Natural Gas |  |  | Water Injection | Selective Catalytic Reduction |  |  | 530
#N/A | #N/A | #N/A |  | 179 | 179 |  |  | #N/A |  | #N/A | #N/A |  | Wallingford Energy, LLC |  | 55517 | CT05 |  | 2009 |  | 401 | 12 | 17779 |  | 0.02 | 1.1 | 175548 | EGU |  | 4911 | Electric Services | PPL Wallingford Energy, LLC (Owner/Operator) | PPL Wallingford Energy, LLC (Owner/Operator) | Murphy, Dennis J (1700) | Boyer, Linda A (500568) (Started Apr 09, 2009) |  |  | Operating | Combustion turbine | Pipeline Natural Gas |  |  | Water Injection | Selective Catalytic Reduction |  |  | 530
#N/A | #N/A | #N/A |  | 180 | 178 |  |  | #N/A |  | #N/A | #N/A |  | Wallingford Energy, LLC |  | 55517 | CT05 |  | 2008 |  | 549 | 12 | 24124 |  | 0.02 | 1.6 | 238892 | EGU |  | 4911 | Electric Services | PPL Wallingford Energy, LLC (Owner/Operator) | PPL Wallingford Energy, LLC (Owner/Operator) | Murphy, Dennis J (1700) (Started Feb 20, 2008) |  |  |  | Operating | Combustion turbine | Pipeline Natural Gas |  |  | Water Injection | Selective Catalytic Reduction |  |  | 530
#N/A | #N/A | #N/A |  | 181 | 182 | 65 |  | #N/A |  | #N/A | #N/A |  | Waterbury Generation |  | 56629 | 10 |  | 2010 |  | 1053 | 12 | 89942 |  | 0.02 | 4.7 | 695321 | EGU |  |  |  | Waterbury Generation, LLC (Owner/Operator) | Waterbury Generation, LLC (Owner/Operator) | McCandless, Timothy (605320) | Donohue, James P (603193) (Started Oct 28, 2010) |  |  | Operating | Combustion turbine | Pipeline Natural Gas | Diesel Oil |  | Water Injection | Selective Catalytic Reduction |  |  | 1800
|  |  |  | 182 | 181 | [7 empty] | Waterbury Generation |  | 56629 | 10 |  | 2009 |  | 519 | 9 | 35378 |  | 0.05 | 5.9 | 324671 | EGU |  |  |  | Waterbury Generation, LLC (Owner/Operator) | Waterbury Generation, LLC (Owner/Operator) | McCandless, Timothy (605320) (Started May 21, 2009) | Vodopivec, Cynthia (603383) (Started Mar 12, 2009) |  |  | Operating (Started 05/15/2009) | Combustion turbine (Started May 15, 2009) | Pipeline Natural Gas | Diesel Oil |  | Water Injection | Selective Catalytic Reduction |  |  | 1800
#N/A | #N/A | #N/A |  | 1: 183; 2: 185; 3: 66; 5: #N/A; 7: #N/A; 8: #N/A; 10: Waterside Power, LLC; 12: 56189; 13: 4; 15: 2010; 17: 68; 18: 6; 21: 0.33; 22: 2.1; 23: 16818; 24: EGU; 28: Waterside Power, LLC (Owner/Operator); 29: Waterside Power, LLC (Owner/Operator); 30: Dearing, David (605897) (Started Jul 26, 2010); 31: Lydon, Matthew (500625) (Started Jul 26, 2010); 34: Operating; 35: Combustion turbine; 36: Diesel Oil; 39: Water Injection; 43: 247
#N/A | #N/A | #N/A |  | 1: 184; 2: 184; 5: #N/A; 7: #N/A; 8: #N/A; 10: Waterside Power, LLC; 12: 56189; 13: 4; 15: 2009; 17: 15; 18: 6; 21: 0.6; 22: 0.5; 23: 3636; 24: EGU; 28: Waterside Power, LLC (Owner/Operator); 29: Waterside Power, LLC (Owner/Operator); 30: DiCristofaro, Don C (602207); 31: Rodriguez, Raymond G (605453) (Started Nov 12, 2009); 34: Operating; 35: Combustion turbine; 36: Diesel Oil; 39: Water Injection; 43: 247
#N/A | #N/A | #N/A |  | 1: 185; 2: 183; 5: #N/A; 7: #N/A; 8: #N/A; 10: Waterside Power, LLC; 12: 56189; 13: 4; 15: 2008; 17: 42; 18: 6; 21: 0.44; 22: 1.3; 23: 10382; 24: EGU; 28: Waterside Power, LLC (Owner/Operator); 29: Waterside Power, LLC (Owner/Operator); 30: DiCristofaro, Don C (602207); 31: Roberts, Ken (3113); 34: Operating; 35: Combustion turbine; 36: Diesel Oil; 39: Water Injection; 43: 247
#N/A | #N/A | #N/A |  | 1: 186; 2: 188; 3: 67; 5: #N/A; 7: #N/A; 8: #N/A; 10: Waterside Power, LLC; 12: 56189; 13: 5; 15: 2010; 17: 73; 18: 6; 21: 0.52; 22: 3.4; 23: 17965; 24: EGU; 28: Waterside Power, LLC (Owner/Operator); 29: Waterside Power, LLC (Owner/Operator); 30: Dearing, David (605897) (Started Jul 26, 2010); 31: Lydon, Matthew (500625) (Started Jul 26, 2010); 34: Operating; 35: Combustion turbine; 36: Diesel Oil; 39: Water Injection; 43: 247
#N/A | #N/A | #N/A |  | 1: 187; 2: 187; 5: #N/A; 7: #N/A; 8: #N/A; 10: Waterside Power, LLC; 12: 56189; 13: 5; 15: 2009; 17: 16; 18: 6; 21: 0.56; 22: 0.6; 23: 3841; 24: EGU; 28: Waterside Power, LLC (Owner/Operator); 29: Waterside Power, LLC (Owner/Operator); 30: DiCristofaro, Don C (602207); 31: Rodriguez, Raymond G (605453) (Started Nov 12, 2009); 34: Operating; 35: Combustion turbine; 36: Diesel Oil; 39: Water Injection; 43: 247
#N/A | #N/A | #N/A |  | 1: 188; 2: 186; 5: #N/A; 7: #N/A; 8: #N/A; 10: Waterside Power, LLC; 12: 56189; 13: 5; 15: 2008; 17: 45; 18: 6; 21: 0.6; 22: 1.7; 23: 11112; 24: EGU; 28: Waterside Power, LLC (Owner/Operator); 29: Waterside Power, LLC (Owner/Operator); 30: DiCristofaro, Don C (602207); 31: Roberts, Ken (3113); 34: Operating; 35: Combustion turbine; 36: Diesel Oil; 39: Water Injection; 43: 247
#N/A | #N/A | #N/A |  | 1: 189; 2: 191; 3: 68; 5: #N/A; 7: #N/A; 8: #N/A; 10: Waterside Power, LLC; 12: 56189; 13: 7; 15: 2010; 17: 69; 18: 6; 21: 0.47; 22: 2.7; 23: 16957; 24: EGU; 28: Waterside Power, LLC (Owner/Operator); 29: Waterside Power, LLC (Owner/Operator); 30: Dearing, David (605897) (Started Jul 26, 2010); 31: Lydon, Matthew (500625) (Started Jul 26, 2010); 34: Operating; 35: Combined cycle; 36: Diesel Oil; 39: Water Injection; 43: 247
#N/A | #N/A | #N/A |  | 1: 190; 2: 190; 5: #N/A; 7: #N/A; 8: #N/A; 10: Waterside Power, LLC; 12: 56189; 13: 7; 15: 2009; 17: 16; 18: 6; 21: 0.54; 22: 0.6; 23: 3866; 24: EGU; 28: Waterside Power, LLC (Owner/Operator); 29: Waterside Power, LLC (Owner/Operator); 30: DiCristofaro, Don C (602207); 31: Rodriguez, Raymond G (605453) (Started Nov 12, 2009); 34: Operating; 35: Combined cycle; 36: Diesel Oil; 39: Water Injection; 43: 247
#N/A | #N/A | #N/A |  | 1: 191; 2: 189; 5: #N/A; 7: #N/A; 8: #N/A; 10: Waterside Power, LLC; 12: 56189; 13: 7; 15: 2008; 17: 44; 18: 6; 21: 0.47; 22: 1.6; 23: 10859; 24: EGU; 28: Waterside Power, LLC (Owner/Operator); 29: Waterside Power, LLC (Owner/Operator); 30: DiCristofaro, Don C (602207); 31: Roberts, Ken (3113); 34: Operating; 35: Combined cycle; 36: Diesel Oil; 39: Water Injection; 43: 247

## A2(SCR)
x
Major Equipment List for an SCR Application
| Item | Description/Size
| SCR reactors (1 to 2) | Vertical flow type, 805,000 acfm capacity, 44 ft.× 44 ft.× 31 ft. high (excluding outlet duct and hoppers), equipped with 9,604 ft3 of ceramic honeycomb catalyst, insulated casing, sootblowers, hoppers, and hoisting mechanism for catalyst replacement
| Anhydrous ammonia tank (1 or more) | Horizontal tank, 250 psig design pressure, storage tanks 15,000 gal, 34-ton storage capacity
| Air compressor (2) | Centrifugal type, rated at 3,200 acfm and 30 hp motor
| Vaporizers (2) | Electrical type, rated at 80 kW
| Mixing chamber | Carbon steel vessel for mixing or air and ammonia
| Ammonia injection grid | Stainless steel construction, piping, valves and nozzles
| Ammonia supply piping diameter, with valves and fittings | Piping for ammonia unloading and supply, carbon steel pipe: 1.0"
| Sootblowing steam | Steam supply piping for the reactor soot-piping blowers, 2" diameter pipe with an on-off control valve and drain and vent valved connections
| Air ductwork | Ductwork between air blowers, mixing chamber, and ammonia injection grid, carbon steel, 14 in. dia., with two isolation butterfly dampers and expansion joints
| Flue gas ductwork | Ductwork modifications to install the SCR modifications reactors, consisting of insulated duct, static mixers, turning vanes, and expansion joints
| Economizer bypass | Ductwork addition to increase flue gas temperature during low loads consisting of insulated duct, flow control dampers, static mixers, turning vanes, expansion joints, and an opening in the boiler casing
| Ash handling | Extension of the existing fly ash handling modifications system: modifications consisting of twelve slide gate valves, twelve material, handling valves, one segregating valve, and ash conveyor piping
| Induced draft fans | Centrifugal type, 650,000 acfm at 34" wg and 4,000 hp motor
| Controls and instrumentation | Stand-alone, microprocessor-based controls for the SCR system with feedback from the plant controls for the unit load, NOx emissions, etc., including NOx analyzers, air and ammonia flow monitoring devices, ammonia sensing and alarming devices at the tank area, and other miscellaneous instrumentation
| Electrical supply | Electrical wiring, raceway, and conduit to connect the new equipment and controls to the existing plant supply systems
| Electrical equipment | System service transformer OA/FA/-60 Hz, 1,000/1,250 kVA (65 C)
| Foundations | Foundations for the equipment and ductwork/piping, as required
| Structural steel | Steel for access to and support of the SCR reactors and other equipment, ductwork, and piping
Source:
EPA AIR POLLUTION CONTROL COST MANUAL, 6th Ed - EPA/452/B-02-001, Jan 2002 - Table 2.2 Page 466

## A4(twn) (hidden)
Table 1
Connecticut Town Numbers |  |  |  | Fuels
No. | Town Name | Air Bureau Town No. | County | No. | Class | Acronym | Remarks / Other Names | Temp (⁰F) | Remarks | Remarks
1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 5 | 7 | 8
1 | Andover | 1 | Tolland | 2: ASTM Class
2 | Ansonia | 2 | New Haven | 1: 1; 2: Distillate fuel oil No. 1; 3: DF-1; 4: coal oil, stove oil, range oil
3 | Ashford | 3 | Windham | 1: 2; 2: Distillate fuel oil No. 2; 3: DF-2; 4: Bunker A, heating oil
4 | Avon | 4 | Hartford | 1: 3; 2: Distillate fuel oil No. 3; 3: DF-3; 4: # 2 per ASTM
5 | Barkhampsted | 5 | Litchfield | 1: 4; 2: Distillate fuel oil No. 4; 3: DF-4; 4: Bunker B
6 | Beacon Falls | 6 | New Haven | 5 | Distillate fuel oil No. 5 | DF-5 | Bunker B, navy special, FFO | 170⁰F - 220⁰F
7 | Berlin | 7 | Hartford | 6 | Distillate fuel oil No. 6 | DF-6 | Bunker C, RFO, PS-400 | 220⁰F - 260⁰F
8 | Bethany | 8 | New Haven | 3: Notes:; 4: RFO - residual fuel oil
9 | Bethel | 9 | Fairfield | 4: FFO - furnace fuel oil
10 | Bethlehem | 10 | Litchfield
11 | Bloomfield | 11 | Hartford | 2: Maritime Class
12 | Bolton | 12 | Tolland | 2: Marine gas oil; 3: MGO; 4: roughly No. 2
13 | Bozrah | 13 | New London | 2: Marine Diesel oil; 3: MDO; 4: blend of heavy gasoil
14 | Branford | 14 | New Haven | 2: Intermediate fuel oil; 3: IFO; 4: blend of gasoil and heavy fuel oil
15 | Bridgeport | 15 | Fairfield | 2: Marine fule oil; 3: MFO; 4: same as HFO
16 | Bridgewater | 25 | Litchfield | 2: Heavy fuel oil; 3: HFO; 4: roughly No. 6
17 | Bristol | 26 | Hartford
18 | Brookfield | 28 | Fairfield
19 | Brooklyn | 29 | Windham
20 | Burlington | 30 | Hartford
21 | Canaan | 31 | Litchfield
22 | Canterbury | 32 | Windham
23 | Canton | 33 | Hartford
24 | Chaplin | 34 | Windham
25 | Cheshire | 35 | New Haven
26 | Chester | 36 | Middlesex
27 | Clinton | 37 | Middlesex
28 | Colchester | 38 | New London
29 | Colebrook | 39 | Litchfield
30 | Columbia | 40 | Tolland
31 | Cornwall | 41 | Litchfield
32 | Coventry | 42 | Tolland
33 | Cromwell | 43 | Middlesex
34 | Danbury | 44 | Fairfield
35 | Darien | 46 | Fairfield
36 | Deep River | 218 | Middlesex
37 | Derby | 47 | New Haven
38 | Durham | 48 | Middlesex
39 | Eastford | 49 | Windham
40 | East Granby | 50 | Hartford
41 | East Haddam | 51 | Middlesex
42 | East Hampton | 52 | Middlesex
43 | East Hartford | 53 | Hartford
44 | East Haven | 54 | New Haven
45 | East Lyme | 55 | New London
46 | Easton | 56 | Fairfield
47 | East Windsor | 57 | Hartford
48 | Ellington | 58 | Tolland
49 | Enfield | 59 | Hartford
50 | Essex | 60 | Middlesex
51 | Fairfield | 61 | Fairfield
52 | Farmington | 62 | Hartford
53 | Franklin | 63 | New London
54 | Glastonbury | 64 | Hartford
55 | Goshen | 65 | Litchfield
56 | Granby | 66 | Hartford
57 | Greenwich | 67 | Fairfield
58 | Griswold | 69 | New London
59 | Groton | 70 | New London
60 | Guilford | 71 | New Haven
61 | Haddam | 72 | Middlesex
62 | Hamden | 73 | New Haven
63 | Hampton | 74 | Windham
64 | Hartford | 75 | Hartford
65 | Hartland | 85 | Hartford
66 | Harwinton | 86 | Litchfield
67 | Hebron | 87 | Tolland
68 | Kent | 88 | Litchfield
69 | Killingly | 89 | Windham
70 | Killingworth | 90 | Middlesex
71 | Lebanon | 91 | New London
72 | Ledyard | 92 | New London
73 | Lisbon | 93 | New London
74 | Litchfield | 94 | Litchfield
75 | Lyme | 95 | New London
76 | Madison | 96 | New Haven
77 | Manchester | 97 | Hartford
78 | Mansfield | 98 | Tolland
79 | Marlborough | 99 | Hartford
80 | Meriden | 100 | New Haven
81 | Middlebury | 102 | New Haven
82 | Middlefield | 103 | Middlesex
83 | Middletown | 104 | Middlesex
84 | Milford | 105 | New Haven
85 | Monroe | 106 | Fairfield
86 | Montville | 107 | New London
87 | Morris | 108 | Litchfield
88 | Naugatuck | 109 | New Haven
89 | New Britain | 110 | Hartford
90 | New Canaan | 114 | Fairfield
91 | New Fairfield | 115 | Fairfield
92 | New Hartford | 116 | Litchfield
93 | New Haven | 117 | New Haven
94 | Newington | 127 | Hartford
95 | New London | 128 | New London
96 | New Milford | 130 | Litchfield
97 | Newtown | 131 | Fairfield
98 | Norfolk | 132 | Litchfield
99 | North Branford | 133 | New Haven
100 | North Canaan | 134 | Litchfield
101 | North Haven | 135 | New Haven
102 | North Stonington | 136 | New London
103 | Norwalk | 137 | Fairfield
104 | Norwich | 139 | New London
105 | Old Lyme | 141 | New London
106 | Old Saybrook | 142 | Middlesex
107 | Orange | 143 | New Haven
108 | Oxford | 144 | New Haven
109 | Plainfield | 145 | Windham
110 | Plainville | 146 | Hartford
111 | Plymouth | 147 | Litchfield
112 | Pomfret | 148 | Windham
113 | Portland | 149 | Middlesex
114 | Preston | 150 | New London
115 | Prospect | 151 | New Haven
116 | Putnam | 152 | Windham
117 | Redding | 153 | Fairfield
118 | Ridgefield | 154 | Fairfield
119 | Rocky Hill | 155 | Hartford
120 | Roxbury | 156 | Litchfield
121 | Salem | 157 | New London
122 | Salisbury | 158 | Litchfield
123 | Scotland | 160 | Windham
124 | Seymour | 161 | New Haven
125 | Sharon | 162 | Litchfield
126 | Shelton | 163 | Fairfield
127 | Sherman | 164 | Fairfield
128 | Simsbury | 165 | Hartford
129 | Somers | 166 | Tolland
130 | Southbury | 167 | New Haven
131 | Southington | 168 | Hartford
132 | South Windsor | 169 | Hartford
133 | Sprague | 170 | New London
134 | Stafford | 171 | Tolland
135 | Stamford | 172 | Fairfield
136 | Sterling | 176 | Windham
137 | Stonington | 177 | New London
138 | Stratford | 178 | Fairfield
139 | Suffield | 179 | Hartford
140 | Thomaston | 180 | Litchfield
141 | Thompson | 181 | Windham
142 | Tolland | 182 | Tolland
143 | Torrington | 183 | Litchfield
144 | Trumbull | 185 | Fairfield
145 | Union | 186 | Tolland
146 | Vernon | 187 | Tolland
147 | Voluntown | 188 | New London
148 | Wallingford | 189 | New Haven
149 | Warren | 190 | Litchfield
150 | Washington | 191 | Litchfield
151 | Waterbury | 192 | New Haven
152 | Waterford | 199 | New London
153 | Watertown | 200 | Litchfield
154 | Westbrook | 201 | Middlesex
155 | West Hartford | 202 | Hartford
156 | West Haven | 203 | New Haven
157 | Weston | 205 | Fairfield
158 | Westport | 206 | Fairfield
159 | Wethersfield | 207 | Hartford
160 | Willington | 208 | Tolland
161 | Wilton | 209 | Fairfield
162 | Winchester | 210 | Litchfield
163 | Windham | 211 | Windham
164 | Windsor | 212 | Hartford
165 | Windsor Locks | 213 | Hartford
166 | Wolcott | 214 | New Haven
167 | Woodbridge | 215 | New Haven
168 | Woodbury | 216 | Litchfield
169 | Woodstock | 217 | Windham

## A2(sm) (hidden)
South Meadows - Cost Analysis
| SCR |  | Total Capital Cost per CRRA Report | [5 empty] | Re calculation without cost multiplier | [7 empty] | Cost Effectiveness - All 8 units | [9 empty] | Cost Effectiveness - All 8 units
Cost allocation |  |  | Cost | x 2 (twin pack) | Twin Pack Item Total | Total Cumulative | Cost factor Col (4)/(2) |  | Cost | x 2 (twin pack) | Item Total | Total Cumulative | SCR Cost Effectiveness Assessment - CRRA Report |  |  |  | Year | Annualized Cost | O&M Cost [4] | Cost Per Year | NOx tons Reduced | Cost Effectiveness $/ton NOx(R) | SCR Cost Effectiveness Assessment - CAIROS data, 15 yrs 9% |  |  |  | Year | Annualized Cost | O&M Cost [4] | Cost Per Year | NOx tons Reduced [5] | Cost Effectiveness $/ton NOx(R)
(col #) | 1 |  | 2 | 3 | 4 | 5 | 6 |  | 7 | 8 | 9 | 10 |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6
1 | Catalyst |  | 149000 | 298000 | 387400 | 1838294 | 1.3 |  | 149000 | 298000 | 298000 | 1596480 | Total Capital Cost (TCC) |  | 18266776 |  | 2011 | 4299999.0704 | 167167 | 4467166.0704 | 9.207 | 485192.3613 | Total Capital Cost (TCC) |  | 16024512 |  | 2011 | 2087382.2064 | 167167 | 2254549.2064 | 10.8 | 208754.5562
1 | Cat Box Steel |  | 92610 | 185220 | 240786 |  | 1.3 |  | 92610 | 185220 | 185220 |  | TCC + 5% PM |  | 19180114.8 |  | 2012 | 4299999.0704 | 172182.01 | 4472181.0804 |  |  | TCC + 5% PM |  | 16825737.6 |  | 2012 | 2087382.2064 | 172182.01 | 2259564.2164
1 | Cat Box Enclosure |  | 42500 | 85000 | 110500 |  | 1.3 |  | 42500 | 85000 | 85000 | [5 empty] | 2013 | 4299999.0704 | 177347.4703 | 4477346.5407 | [6 empty] | 2013 | 2087382.2064 | 177347.4703 | 2264729.6767
6 | Fan Base Steel |  | 4030 | 8060 | 10478 |  | 1.3 |  | 4030 | 8060 | 8060 |  | Equipmet Life |  | 5 |  | 2014 | 4299999.0704 | 182667.8944 | 4482666.9648 |  |  | Equipmet Life |  | 15 |  | 2014 | 2087382.2064 | 182667.8944 | 2270050.1008
6 | Duct supports |  | 22600 | 45200 | 58760 |  | 1.3 |  | 22600 | 45200 | 45200 |  | Interest |  | 0.06 |  | 2015 | 4299999.0704 | 188147.9312 | 4488147.0016 |  |  | Interest |  | 0.09 |  | 2015 | 2087382.2064 | 188147.9312 | 2275530.1377
7 | Ductwork |  | 90000 | 180000 | 234000 |  | 1.3 |  | 90000 | 180000 | 180000 |  | Capital Recovery Factor (CRF) |  | 0.2374 | [1] | 1: 2016; 3: 193792.3692; 4: 193792.3692 | Capital Recovery Factor (CRF) |  | 0.12406 | [1] | 2016 |  | 193792.3692 | 193792.3692
7 | Insul and Cladding |  | 36000 | 72000 | 93600 |  | 1.3 |  | 36000 | 72000 | 72000 |  | CRF selected |  | 0.2354 | [2] | [6 empty] | CRF selected |  | 0.12406 | [2]
2 | Fans |  | 10000 | 20000 | 26000 |  | 1.3 |  | 10000 | 20000 | 20000
2 | Tank |  | 30100 | 30100 | 39130 |  | 1.3 |  | 30100 | 60200 | 60200 |  | Annualized Cost - 2009 Operation Estimate - 8 units |  | 4299999.0704 | [3] | 1: Cost Effectiveness - per unit | Annualized Cost - Operation Estimate - 8 units |  | 2087382.2064 | [3] | Cost Effectiveness - per unit
3 | Dist Module |  | 23400 | 46800 | 60840 |  | 1.3 |  | 23400 | 46800 | 46800 |  | Annualized Cost- 2009 Op - per unit |  | 537499.8838 |  | 2011 | 537499.8838 | 20895.875 | 558395.7588 | 1.1509 | 485192.3613 | Annualized Cost-per unit |  | 260922.7758 |  | 2011 | 260922.7758 | 20895.875 | 281818.6508 | 1.35 | 208754.5562
3 | Metering Skid |  | 90000 | 90000 | 117000 |  | 1.3 |  | 90000 | 180000 | 180000
2 | Injectors |  | 18900 | 37800 | 49140 |  | 1.3 |  | 18900 | 37800 | 37800 |  | Note: |  |  |  | 1: Annual O&M breakdown | Note: |  |  |  | Annual O&M breakdown
2 | Injector Retract |  | 34300 | 68600 | 89180 |  | 1.3 |  | 34300 | 68600 | 68600 |  | [1] | Per Engineering Economic Analysis tables Schaum's Outline Series, McGraw-Hill |  |  | 1: Catalyst Replacement; 4: 55343 | [1] | Per Engineering Economic Analysis tables Schaum's Outline Series, McGraw-Hill |  |  | Catalyst Replacement |  |  | 55343
4 | Cont Panel |  | 14400 | 28800 | 37440 |  | 1.3 |  | 14400 | 28800 | 28800 | [5 empty] | 1: Electrical load; 4: 97 |  |  |  |  | Electrical load |  |  | 97
4 | Retract Panel |  | 5400 | 10800 | 14040 |  | 1.3 |  | 5400 | 10800 | 10800 |  | [2] | CRRA used CRF=0.2354 instead of 0.2374 for annualized cost |  |  | 1: Urea; 4: 4830 |  |  |  |  | Urea |  |  | 4830
| Building |  | 40000 |  | 40000 |  |  |  | 40000 |  | 40000 |  | [3] | For 2009 Operation Annualized Cost, CRRA used TCC x CRF, instead of (TCC +5%PM) x CRF as stated in report |  |  | 1: Labor (Ops, Maint, Admin); 4: 100000 | [3] | For 2009 Operation Annualized Cost, CRRA used TCC x CRF, instead of (TCC +5%PM) x CRF as stated in report |  |  | Labor (Ops, Maint, Admin) |  |  | 100000
| Engineering |  |  |  | 230000 | [5 empty] | 230000 | [5 empty] | 1: Maint Materials; 4: 6897 |  |  |  |  | Maint Materials |  |  | 6897
| Contingency (10% Total Cost) |  | 184000 | 368000 | 478400 |  | 1.3 |  |  | 159648 | 159648 |  | [4] | O&M Cost was increased with 3% beyond 2011, for each year |  |  | 1: Annual O&M Cost; 4: 167167 | [4] | O&M Cost was increased with 3% beyond 2011, for each year |  |  | Annual O&M Cost |  |  | 167167
| Total 1 Twin Pack |  |  |  | 2316694 | [5 empty] | 1756128
| Total 4 Twin Pack | 4 |  |  | 9266776 | [5 empty] | 7024512 | [5 empty] | 1: Project Management @ 5% TCC; 4: 913338.8 |  |  |  |  | Project Management @ 5% TCC |  |  | 801225.6
| Installation (est) | 4 |  | 2250000 | 9000000 |  |  |  |  | 2250000 | 9000000 | [5 empty] | 1: (first year only) |  |  |  |  | (first year only)
| Project Total |  |  |  | 18266776 | [5 empty] | 16024512 | [5 empty] | 3: Total (first year only); 4: 1080505.8 | [6 empty] | Total (first year only) | 968392.6
Summary of Results
[5 empty] | 1 Twin Pack | Total 4 Twin Packs
| Equipment Cost (equipment + auxiliary accesories) |  |  |  | 1568294 | 6273176 |  |  | Contingency %
| Construction / Building |  |  |  | 40000 | 160000
[6 empty] | 6433176 |  | 6433176 | 0.29746
| Engineering |  |  |  | 230000 | 920000
| Installation (direct + indirect) |  |  |  |  | 9000000
| Total Ditect + Indirect Costs |  |  |  |  | 9920000 |  | 9920000
| Contingency |  |  |  | 478400 | 1913600
| Total Contingency |  |  |  |  | 1913600 |  | 16353176 | 0.11702
18266776
| HPWI |  | Total Capital Cost per CRRA Report | [13 empty] | 1: Cost Effectiveness - All 8 units |  |  |  |  | Cost Effectiveness - All 8 units
|  |  | Cost | x 2 (twin pack) | Twin Pack Item Total | Total Cumulative | % Cost | [5 empty] | HPWI Cost Effectiveness Assessment - CRRA Report |  |  |  | Year | Annualized Cost | O&M Cost [4] | Cost Per Year | NOx tons Reduced | Cost Effectiveness $/ton NOx(R) | HPWI Cost Effectiveness Assessment - CAIROS data, 15 yrs 9% |  |  |  | Year | Annualized Cost | O&M Cost [4] | Cost Per Year | NOx tons Reduced | Cost Effectiveness $/ton NOx(R)
| 1 |  | 2 | 3 | 4 | 5 | 6 | [9 empty] | 1 | 2 | 3 | 4 | 5 | 6 |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6
1 | HPWI System |  |  |  | 1154000 | 4549000 | [6 empty] | Total Capital Cost (TCC) |  | 11853900 |  | 2011 | 2790408.06 | 124573 | 2914981.06 | 6.138 | 474907.3086 | Total Capital Cost (TCC) |  | 11853900 |  | 2011 | 1470581.589 | 124573 | 1595154.589 | 7.2 | 221549.2485
| Engine Mods |  |  |  | 1600000 | [7 empty] | TCC + 5% PM |  | 12446595 |  | 2012 | 2790408.06 | 128310.19 | 2918718.25 |  |  | TCC + 5% PM |  | 12446595 |  | 2012 | 1470581.589 | 128310.19 | 1598891.779
| Controls Add |  |  |  | 115000 | [11 empty] | 2013 | 2790408.06 | 132159.4957 | 2922567.5557 | [6 empty] | 2013 | 1470581.589 | 132159.4957 | 1602741.0847
| Tank |  |  |  | 30000 | [7 empty] | Equipmet Life |  | 5 |  | 2014 | 2790408.06 | 136124.2806 | 2926532.3406 |  |  | Equipmet Life |  | 15 |  | 2014 | 1470581.589 | 136124.2806 | 1606705.8696
| Bldg x 4 |  |  |  | 160000 | [7 empty] | Interest |  | 0.06 |  | 2015 | 2790408.06 | 140208.009 | 2930616.069 |  |  | Interest |  | 0.09 |  | 2015 | 1470581.589 | 140208.009 | 1610789.598
| Demineralizer |  |  |  | 1250000 | [7 empty] | Capital Recovery Factor (CRF) |  | 0.2374 | [1] | 1: 2016; 3: 144414.2493; 4: 144414.2493 | Capital Recovery Factor (CRF) |  | 0.12406 | [1] | 2016 |  | 144414.2493 | 144414.2493
| Coordination Eng 5% |  |  |  | 240000 |  | 0.055697 | [5 empty] | CRF selected |  | 0.2354 | [2] | [6 empty] | CRF selected |  | 0.12406 | [2]
| Contingency 10% |  |  |  | 454900 |  | 0.1
| Total 4 Twin Pack |  |  |  | 5003900 | [7 empty] | Annualized Cost - 2009 Operation Estimate - 8 units |  | 2790408.06 | [3] | 1: Cost Effectiveness - per unit | Annualized Cost - Operation Estimate - 8 units |  | 1470581.589 | [3] | Cost Effectiveness - per unit
| Installation (Budget Quote) |  |  |  | 6850000 |  | 1.3689 | [5 empty] | Annualized Cost- 2009 Op - per unit |  | 348801.0075 |  | 2011 | 348801.0075 | 15571.625 | 364372.6325 | 0.76725 | 474907.3086 | Annualized Cost- 2009 Op - per unit |  | 183822.6986 |  | 2011 | 183822.6986 | 15571.625 | 199394.3236 | 0.9 | 221549.2485
| ProiectTotal |  |  |  | 11853900
[13 empty] | Note: |  |  |  | 1: Annual O&M breakdown | Note: |  |  |  | Annual O&M breakdown
[5 empty] | 4149000 | [7 empty] | [1] | Per Engineering Economic Analysis tables Schaum's Outline Series, McGraw-Hill |  |  | 1: Resin; 4: 16800 | [1] | Per Engineering Economic Analysis tables Schaum's Outline Series, McGraw-Hill |  |  | Resin |  |  | 16800
[17 empty] | 1: Electrical load; 4: 841 |  |  |  |  | Electrical load |  |  | 841
[13 empty] | [2] | CRRA used CRF=0.2354 instead of 0.2374 for annualized cost |  |  | 1: Water; 4: 35 | [2] | CRRA used CRF=0.2354 instead of 0.2374 for annualized cost |  |  | Water |  |  | 35
[5 empty] | 1481737.5 | [7 empty] | [3] | For 2009 Operation Annualized Cost, CRRA used TCC x CRF, instead of (TCC +5%PM) x CRF as stated in report |  |  | 1: Labor (Ops, Maint, Admin); 4: 100000 | [3] | For 2009 Operation Annualized Cost, CRRA used TCC x CRF, instead of (TCC +5%PM) x CRF as stated in report |  |  | Labor (Ops, Maint, Admin) |  |  | 100000
[17 empty] | 1: Maint Materials; 4: 6897 |  |  |  |  | Maint Materials |  |  | 6897
[13 empty] | [4] | O&M Cost was increased with 3% beyond 2011, for each year |  |  | 1: Annual O&M Cost; 4: 124573 | [4] | O&M Cost was increased with 3% beyond 2011, for each year |  |  | Annual O&M Cost |  |  | 124573
[17 empty] | 1: Project Management @ 5% TCC; 4: 592695 |  |  |  |  | Project Management @ 5% TCC |  |  | 592695
[17 empty] | 1: (first year only) |  |  |  |  | (first year only)
[17 empty] | 3: Total (first year only); 4: 717268 | [6 empty] | Total (first year only) | 717268

## A3(trc) (hidden)
[15 empty] | TRC | FirstLight
Norwich
PSEG
[16 empty] | n | 20 | NH10
[16 empty] | I % | 0.07
[16 empty] | CRF | 0.094393 |  | NRG |  |  |  | EPA |  |  |  | Adjusted
[19 empty] | 2009 | 2010 | 2008 |  | 2008 | 2009 | 2010 |  | 2008 | 2009 | 2010
[18 empty] | Operating Hours | 5.9 | 23.1 |  | Operating Hours |  |  |  | Operating Hours
[16 empty] | 119.6 |  | OS Hrs | 4.1 | 17.5 |  | OS Hrs | 8 | 6 | 21 | OS Hrs | 8 | 6 | 21
FirstLight Hydro Generating Company | [11 empty] | FirstLight | 8303-01 | 1 | SCR + HPWI + CO Catalyst + Dual Fuel |  |  | Non OS Hrs | 1.8 | 5.5
[18 empty] | Check | 5.9 | 23
|  |  | Average Fuel Use Rate | 249 | MMBtu/hr | [9 empty] | (Natural Gas with Oil backup)
|  |  | Annual Total Hours of Operation | 50 | hrs | [9 empty] | 5 ppmvd - 4.46 ton/yr NOx reduction |  |  |  | 2009 | 2010
|  |  | Heat Input | 12450 | MMBtu/yr | [9 empty] | 6310000 | 5 | 4.46 | Heat Input/yr | 1650 | 5310 |  | Heat Input/yr |  |  |  | Heat Input/yr
|  |  | (Uncontrolled) NOx Emission Rate | 0.736 | lb/MMBtu |  | 0.73066 | [7 empty] | 315500 | 0.95819 | 4.6546 |  |  |  |  | Heat Input/OS |  | 4 | 13 | Heat Input/OS | 2042.1223 | 1677.9661 | 4848.2609
|  |  |  | 186.7072 | ppm | [9 empty] | 190292 | 252400 | [5 empty] | NOx Rate |  |  |  | NOx Rate | 0.514 | 0.514 | 0.514
|  |  | (Uncontrolled) NOx Emission (tons/yr) | 4.5816 | tons/yr | [8 empty] | 2 | SCR + HPWI + CO Catalyst |  |  | Heat Input/yr-hr | 279.661 | 230.8696 | 255.2653 | Gross Load | 67 | 55 | 204 | Gross Load | 67 | 55 | 204
[15 empty] | (Primary fuel Oil - Kerosene K1) | [6 empty] | NOx Tons | 0.12 | 0 | 0 | NOx Tons | 0.52483 | 0.43124 | 1.246
[15 empty] | 10 ppmvd - 4.33 ton/yr NOx reduction |  |  | Heat Input/OS | 1146.6102 | 4040.2174
|  |  |  | Controlled NOx Rate | η % | Controlled NOx Rate | Controlled NOx | Removed NOx | [6 empty] | 3630000 | 10 | 4.33 |  |  |  |  | NOx/MWh | 1791.0448 | 0 | 0 | NOx/MWh | 7833.2155 | 7840.678 | 6107.8581
[15 empty] | 181500 | 0.91639 | 4.7251
|  | 1 | Dual Fuel + HPWI+SCR+CO | 5 | 0.97322 | 0.01971 | 0.12269 | 4.4589 | [6 empty] | 112635 | 145200
|  | 2 | HPWI+SCR+CO | 10 | 0.94644 | 0.03942 | 0.24539 | 4.3362 | [5 empty] | 3 | Selective Catalytic Reduction (SCR)
|  | 3 | SCR | 25 | 0.8661 | 0.09855 | 0.61347 | 3.9681 | [6 empty] | (Primary fuel Oil - Kerosene K1)
|  | 4 | CC-AD + HPWI | 50 | 0.7322 | 0.1971 | 1.2269 | 3.3547 | [6 empty] | 25 ppmvd - 3.96 ton/yr NOx reduction |  |  | MV10
|  | 5 | HPWI | 75 | 0.5983 | 0.29565 | 1.8404 | 2.7412 | [6 empty] | 2730000 | 25 | 3.96 |  | NRG |  |  |  | Adjusted
|  | 6 | Dual Fuel NatGas + Oil | 120 | 0.35728 | 0.47304 | 2.9447 | 1.6369 | [6 empty] | 136500 | 0.79097 | 5.0065 |  | 2009 | 2010 | AVG |  | 2009 | 2010 | AVG
|  | 7 | New Eqp - GE on Nat Gas | 25 | 0.8661 | 0.09855 | 0.61347 | 3.9681 | [6 empty] | 92753 | 109200 |  | Operating Hours | 133.4 | 338.5 | 235.95 | Operating Hours | 133.4 | 338.5 | 235.95
|  | 8 | New Eqp - GE | 42 | 0.77505 | 0.16556 | 1.0306 | 3.551 | [5 empty] | 4 | HPWI with Cookie Cutter Air Deflectors |  |  | OS Hrs | 19.6 | 98 |  | OS Hrs | 111.5 | 316.2 | 213.85
[15 empty] | (Primary fuel Oil - Kerosene K1) |  |  | Non OS Hrs | 21.9 | 22.3 |  | Non OS Hrs | 21.9 | 22.3
[15 empty] | 50 ppmvd - 3.33 ton/yr NOx reduction |  |  | Check | 41.5 | 120.3 | 235.95 | Check | 133.4 | 338.5 | 235.95
|  | No. | Description NOX COntrol System | Tag |  |  |  | TCC | [6 empty] | 1005000 | 50 | 3.33
[15 empty] | 50250 | 0.58194 | 5.7222 |  | 2009 | 2010 | AVG |  |  | Heat Input (MMBtu/hr) | 29
|  | 1 | Convert To Natural Gas | NG |  |  |  | 1500000 | [6 empty] | 40565 | 40200 |  | NOx (reported) | - | - | 6 |  |  | Stack Test Rate (lb/MMBtu) | 3.09
|  | 2 | Turbine Modifications | Mod |  |  |  | 1000000 | [5 empty] | 5 | High Pressure Water Injection (HPWI) | [8 empty] | NOx (tons) AVG /yr | 10.5717 |  |  |  |  | Typical speeds are 330 m/s in air, 1450 m/s in water and about 5000 m/s in granite.
|  | 3 | Selective Catalytic Reduction | SCR |  |  |  | 2550000 | [6 empty] | (Primary fuel Oil - Kerosene K1) |  |  |  |  | MV10 resulted (hourly) NOx rate | 0.025429
|  | 4 | CO Catalyst | CO |  |  |  | 200000 | [6 empty] | 75 ppmvd - 2.70 ton/yr NOx reduction
|  | 5 | HPWI + well | HPWI |  |  |  | 700000 | [6 empty] | 880000 | 75 | 2.7 | [5 empty] | 2009 | 2010 | AVG |  |  |  |  | 5000 | 450 | 1600 | 720000 | 144
|  | 6 | New Eqp - GE | NEqp NG |  |  |  | 12000000 | [6 empty] | 44000 | 0.37291 | 7.2404 |  |  |  |  | OS hrs | 111.5 | 316.2 | 213.85 | [8 empty] | 2.4
|  | 7 | Cookie Cutter Air delection | CC-AD |  |  |  | 125000 | [6 empty] | 43744 | 35200 | [5 empty] | NOx (tons) | 4.9958 | 14.1673 | 9.5815 |  |  |  |  | 5000 | 3.1 | 1612.9032
[14 empty] | 6 | LM2500 DLE - new gas fired GE turbine
Option |  | Option | Description NOX COntrol System |  |  | Lost Rev | Salv Value | TCC | [6 empty] | (Natural Gas with Oil backup)
Sel |  | stk | [12 empty] | 25 ppmvd - 3.97 ton/yr NOx reduction |  |  | MV11
1 |  | 1 | Dual Fule + HPWI+SCR+CO | 1+2+3+4+5 |  | 360000 |  | 6310000 | [6 empty] | 12360000 | 25 | 3.97 |  | NRG |  |  |  | Adjusted | [6 empty] | 2000 | 450 | 1612 | 725400 | 362.7
2 |  | 2 | HPWI+SCR+CO | 3+4+5 |  | 180000 |  | 3630000 | [6 empty] | 618000 | 0.79097 | 5.0192 |  | 2009 | 2010 | AVG |  | 2009 | 2010 | AVG | [8 empty] | 6.045
3 |  | 3 | SCR | 3 |  | 180000 |  | 2730000 | [6 empty] | 418610 | 494400 |  | Operating Hours | 133.4 | 163.6 | 148.5 | Operating Hours | 133.4 | 163.6 | 148.5 |  |  |  |  | 2000 | 1612 | 1.2407
4 |  | 6 | CC-AD + HPWI | 5+7 |  | 180000 |  | 1005000 | [5 empty] | 7 | LM2500 - new oil fired GE turbine |  |  | OS Hrs | 20.4 | 113.5 |  | OS Hrs | 43.8 | 113.5 | 78.65 |  |  |  |  | 5000 | 1612 | 3.1017
5 |  | 7 | HPWI | 5 |  | 180000 |  | 880000 | [6 empty] | (Primary fuel Oil - Kerosene K1) |  |  | Non OS Hrs | 89.6 | 50.1 |  | Non OS Hrs | 89.6 | 50.1 | [5 empty] | 8000 | 1612 | 4.9628
6 |  | 8 | Dual Fuiel NatGas + Oil | 1 |  | 360000 |  | 2860000 | [6 empty] | 42 ppmvd - 3.55 ton/yr NOx reduction |  |  | Check | 110 | 163.6 | 148.5 | Check | 133.4 | 163.6 | 148.5
7 |  | 4 | New Eqp - GE on Nat Gas | 1+6 |  | 360000 | 1500000 | 12360000 | [6 empty] | 10860000 | 42 | 3.55
8 |  | 5 | New Eqp - GE | 6 |  | 360000 | 1500000 | 10860000 | [6 empty] | 543000 | 0.64883 | 5.4714 |  | 2009 | 2010 | AVG |  |  | Heat Input (MMBtu/hr) | 29
[15 empty] | 411017 | 434400 |  | NOx (reported) | - | - | 6 |  |  | Stack Test Rate (lb/MMBtu) | 1.93
[24 empty] | NOx (tons) AVG /yr | 4.1558
[16 empty] | 141.31 |  |  |  | MV10 resulted (hourly) NOx rate | 0.040404
Norwich Public Untilities | [11 empty] | Norwich Public Untilities | 8304-01 |  | SCR + HPWI + Dual Fuel
[15 empty] | 6 ppmvd - 2.62 ton/yr NOx reduction | [7 empty] | 2009 | 2010 | AVG
|  |  | Average Fuel Use Rate | 198 | MMBtu/hr | [9 empty] | 7319263 | 6 | 2.62 |  |  |  |  | OS hrs | 43.8 | 113.5 | 78.65
|  |  | Annual Total Hours of Operation | 50 | hrs | [9 empty] | 389322.5 | 0.95754 | 2.7362 |  |  |  |  | NOx (tons) | 1.2257 | 3.1763 | 2.201
|  |  | Heat Input | 9900 | MMBtu/yr |  | 0.55704 | [7 empty] | 347672 | 219578
|  |  | (Uncontrolled) NOx Emission Rate | 0.553 | lb/MMBtu | [9 empty] | SCR + Water Injection (HPWI)
|  |  |  | 141.31 | ppm | [9 empty] | 9 ppmvd - 2.56 ton/yr NOx reduction
|  |  | (Uncontrolled) NOx Emission (tons/yr) | 2.7374 | tons/yr | [9 empty] | 4554325 | 9 | 2.56 | BR10
[15 empty] | 242251.3298 | 0.93631 | 2.7341 |  | 360000
[15 empty] | 221348 | 136629 |  |  | 250000
|  |  |  | Controlled NOx Rate | η % | Controlled NOx Rate | Controlled NOx | Removed NOx | [6 empty] | Selective Catalytic Reduction (SCR) |  |  |  | 134000
[15 empty] | (Primary fuel No. 2 oil) |  |  |  | 25000
|  | 1 | NG + SCR + HPWI | 6 | 0.95754 | 0.02348 | 0.11623 | 2.6211 | [6 empty] | 25 ppmvd - 2.24 ton/yr NOx reduction |  |  |  | 42000
|  | 2 | SCR + HPWI | 9 | 0.93631 | 0.03522 | 0.17434 | 2.563 | [6 empty] | 3386773 | 25 | 2.24 |  | 2900
|  | 3 | SCR | 25 | 0.82308 | 0.097835 | 0.48428 | 2.2531 | [6 empty] | 180147.5 | 0.82308 | 2.7215 |  | 40000
|  | 4 | HPWI | 47 | 0.6674 | 0.18393 | 0.91045 | 1.8269 | [6 empty] | 187812 | 101603 |  |  | 16000
|  | 5 | Convert To Dual Fuel (Natural Gas + Oil backup) | 90 | 0.3631 | 0.3522 | 1.7434 | 0.99394 | [6 empty] | High Pressure Water Injection (HPWI) |  |  |  | 10000
|  | 6 | NEqp (Dual fuel) | 15 | 0.89385 | 0.058701 | 0.29057 | 2.4468 | [6 empty] | (Primary fuel No. 2 oil) |  |  |  | 40000
|  | 7 | (New turbine) Solar Titan 130 - liquid fuel only | 65 | 0.54002 | 0.25437 | 1.2591 | 1.4782 | [6 empty] | 47 ppmvd - 1.81 ton/yr NOx reduction |  |  |  | 15000 | 934900
[15 empty] | 1191552 | 47 | 1.81 |  | 100000
[15 empty] | 63380.4255 | 0.6674 | 2.712 |  | 50000
[15 empty] | 81969 | 35747 |  |  | 56094 | 0.06 | 934900
|  | No. | Description NOX COntrol System | Tag | Table No. |  |  | TCC | [6 empty] | Solar Tital 130 - new dual fuel w/ SoLoNOx |  |  |  | 1140994
(Natural Gas with Oil backup)
|  | 1 | Convert To Dual Fuel (Natural Gas + Oil backup) | NG | 2 |  |  | 2764939 | [6 empty] | 15 ppmvd - 2.45 ton/yr NOx reduction
|  | 2 | Selective Catalytic Reduction | SCR | 3 |  |  | 3362773 | [6 empty] | 13622600 | 15 | 2.45
|  | 3 | (High Pressure) Water Injection | HPWI | 4 |  |  | 1047552 | [6 empty] | 724606.383 | 0.89385 | 2.741
|  | 4 | (New turbine) Solar Titan 130 - liquid fuel only | NEqp(Lq) | 5 |  |  | 11209875 | [6 empty] | 692571 | 408678
|  | 5 | (New turbine) Solar Titan 130 - dual fuel | NEqp(dual fuel) | 6 |  |  | 14834600
Option |  | Option | Description NOX COntrol System |  |  | Lost Rev | Salv Value | TCC
Sel |  | stk
1 |  | 1 | NG + SCR + HPWI | 2+3+4 | 7 | 144000 |  | 7319264
2 |  | 2 | SCR + HPWI | 3+4 | 8 | 144000 |  | 4554325
3 |  | 4 | SCR | 3 | 9 | 24000 |  | 3386773
4 |  | 5 | HPWI | 4 | 10 | 144000 |  | 1191552
5 |  | 7 | Convert To Dual Fuel (Natural Gas + Oil backup) | 2 | 11 | 144000 |  | 2908939
6 |  | 3 | NEqp (Dual fuel) | 6 | 12 | 288000 | 1500000 | 13622600
7 |  | 6 | (New turbine) Solar Titan 130 - liquid fuel only | 5 | 13 | 288000 | 1500000 | 9997875
[12 empty] | PSEG | 8301-01 |  | Selective Catalytic Reduction (SCR)
[5 empty] | 0.704 | 9319 | 178.5895
[5 empty] | 0.553 | 9319 | 140.2841 | [7 empty] | η ≈ 90% - 25 ppmvd NOx rate
[5 empty] | 0.698 | 9319 | 177.0674 | [7 empty] | 8895118 | 25
[5 empty] | 0.736 | 9319 | 186.7072 | [7 empty] | 404323.5455
839358
[7 empty] | 253.6782 | [7 empty] | High Pressure Water Injection (HPWI)
η ≈ 40% to 70% - 75 ppmvd NOx rate
Waldon Engineering & Construction | [14 empty] | 843728 | 50
Table 3 - NPU - Cost to Implement SCR | [14 empty] | 38351.2727
[15 empty] | 118997 | 5000
A. | Engineering, Procurement, Construction & Start-up
1 | Engineering |  |  | 189075 |  | 0.10496 |  |  | 40452
2 | Procurement |  |  | 1801351 | 1954399 |  |  |  | 287415 |  |  | 0.14074 | 401087
3 | Construction Directs |  |  | 562086 |  | 0.31204 |  |  | 386785 |  |  | 1.3457
4 | Construction Indirects |  |  | 0
5 | Commisioning & Startup |  |  | 73012 |  | 0.040532 | 415135 |  | 65484 | 154124 |  | 0.22784
6 | Construction Management |  |  | 153048 |  | 0.084963 |  |  | 48188 |  |  | 0.16766
| Subtotal A |  |  | 2778572 | 2778572 |  |  |  | 828324 | 828324
[13 empty] | A1 |  | 1801351 | 287415
B. | Sales Tax & Contingency factors | [11 empty] | A2 |  | 562086 | 386785
1 | Sales Tax | [11 empty] | A |  | 2363437 | 674200
2 | Estimating Contingency - 8% A |  |  | 222286 |  | 0.08 |  |  | 66266 |  | 0.08
3 | Economic Cobditions factor | [11 empty] | B | 0.05 | 118171.85 | 33710
4 | Labor availability Factor | [12 empty] | 0.1 | 236343.7 | 67420
5 | Site Indirect | [12 empty] | 0.05 | 118171.85 | 33710
6 | Project factor | [11 empty] | Total B - CI |  | 472687.4 | 134840
7 | Escalation | [11 empty] | Total A+B |  | 2836124.4 | 809040
| Subtotal B |  |  | 222286 | 222286 |  |  |  | 66266 | 66266
[13 empty] | C - Contingency | 0.15 | 425418.66 | 121356
C | Construction Contingency
1 | Contingency |  | 10% A3 | 56209 | [8 empty] | D |  | 3261543.06 | 930396
| Subtotal C |  |  | 56209 | 56209 | 0.1 |  |  | 38679 | 38679 | 0.1
[13 empty] | Pre-prod | 0.02 | 65230.8612 | 18607.92
D. | Overhead
1 | Overhead |  | 5% (A+B+C) | 152853 |  |  | C |  | 46663
2 | Profit |  | 5% (A+B+C) | 152853 |  |  | 584201 |  | 46663 |  | 198271
|  |  |  | 305706 | 305706 |  |  |  | 93326 | 93326 |  |  |  |  | 3326773.9212 | 949003.92
[15 empty] | 0.010821 | 0.081761
[5 empty] | 3362773 |  |  |  |  | 1026595

## ac (hidden)
870.7845
1 | Annual Direct Costs Factors
2
3 | No. | Control Type | Code | Total Variable Cost/MMBtu |  | M/hr
4 |  |  |  | TVC./HI | Remark | Constant | Exp | Remarks
5 |  |  |  | $/MMBtu |  | $/hr
6 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
7 | 1 | HPWI | 1 | 7 | based on most likely value of NRG - HPWI data | 250 | 0 | Constant | based on most likely value of NRG - HPWI data
8 | 2 | ULSF | 1 | 7 | considered same as above | 250 | 0 | Constant | considered same as above
9 | 3 | Nat Gas | 1 | 7 | considered same as above | 250 | 0 | Constant | considered same as above
10 | 4 | SCR | 2 | 0.3 | based on max. value of the average group of NRG data | 13503 | -0.931 | Variable | based on NRG data plot
11 | 5 | New Eqp | 2 | 0.3 | considered same as above | 13503 | -0.931 | Variable | considered same as above
|  |  |  | 250 |  | 250 | 7 | 79.0584 | 0.3
OPERATION REFERENCE # 2
|  |  |  | Avg Op. Time/yr | Heat Input Avg per Unit | (M)/hrs operation | TVC/MMBtu HI | (M)/hrs operation | TVC/MMBtu HI | Mscr
|  | 8300-01-01 | 1 | 29 | 7735 | 241.3793 | 6.1363
|  | 8300-07-01 | 1 | 38.8 | 9915 | 180.4124 | 4.8063
|  | 8300-08-01 | 1 | 29.5 | 8325 | 237.2881 | 5.7027
|  | 8300-09-01 | 1 | 99.9 | 20980 | 70.0701 | 2.2818
|  | 8300-10-01 | 1 | 14.5 | 3480 | 482.7586 | 13.4369
|  | 8300-11-01 | 2 | 20.55 | 4855 |  |  | 0 | 2.0544
|  | 8300-11-02 | 1 | 20.55 | 4855 | 340.6326 | 9.6648
|  | 8300-12-01 | 2 | 80.7 | 31287.5 |  |  | 0 | 0.82998
| 2: 8300-16-01; 3: 2; $/MMBtu 4: 235.95; $/hr 8: 84.7637; $/hr 9: 0 | 83.4324
|  | 8306-01-01 | 2 | 1331.1 | 1017740 |  |  | 18.7815 | 0.14511 | 16.6644
|  | 8306-01-02 | 2 | 1331.1 | 1017740 |  |  | 11.2689 | 0.15268 | 16.6644
|  | 8306-02-01 | 2 | 731.05 | 1233270 |  |  | 6.8395 | 0.27595 | 29.1136 | 16.6644
|  | 8306-02-02 | 2 | 731.05 | 1233270 |  |  | 27.3579 | 0.15004 | 29.1136 | 22182.0053
|  | 8306-03-01 | 2 | 243.6 | 557770 |  |  | 82.1018 | 0.29173 | 80.9904
|  | 8306-03-02 | 2 | 243.6 | 557770 |  |  | 82.1018 | 0.19488 | 80.9904
|  | 8306-03-03 | 2 | 243.6 | 557770 |  |  | 82.1018 | 0.085955 | 80.9904
|  | 8306-04-01 | 2 | 573.9 | 352730 |  |  | 34.8493 | 0.012806 | 36.4715
|  | 8306-04-02 | 2 | 573.9 | 352730 |  |  | 34.8493 | 0.39026 | 36.4715
|  | 8306-04-03 | 2 | 573.9 | 352730 |  |  | 8.1896 | 0.15996 | 36.4715
|  | 8306-05-01 | 2 | 231.15 | 448035 |  |  | 86.5239 | 0.36536 | 85.0443
|  | 8306-05-02 | 2 | 231.15 | 448035 |  |  | 86.5239 | 0.23508 | 85.0443
|  | 8306-05-03 | 2 | 231.15 | 448035 |  |  | 86.5239 | 0.10311 | 85.0443
|  | 8306-06-01 | 2 | 418.45 | 299765 |  |  | 11.9489 | 0.017824 | 48.9418
|  | 8306-06-02 | 2 | 418.45 | 299765 |  |  | 47.7954 | 0.20758 | 48.9418
|  | 8306-07-01 | 2 | 565.35 | 370125 |  |  | 8.8441 | 0.015219 | 36.9848
|  | 8306-07-02 | 2 | 565.35 | 370125 |  |  | 35.3763 | 0.21856 | 36.9848
[6 empty] | 249.9281 | 6.5775
[6 empty] | 258.7569 | 7.0048
[5 empty] | 4855 |  |  |  | 2.0544
[5 empty] | 31287.5 |  |  |  | 0.82998
|  |  |  | 235.95 |  |  |  | 84.7637
|  |  |  | 1331.1 | 1017740 |  |  | 18.7815 | 0.14511
|  |  |  | 1331.1 | 1017740 |  |  |  | 0.15268
|  |  |  | 731.05 | 1233270 |  |  |  | 0.27595
|  |  |  | 731.05 | 1233270 |  |  | 27.3579 | 0.15004
|  |  |  | 243.6 | 557770 |  |  | 82.1018 | 0.29173
|  |  |  | 243.6 | 557770 |  |  | 82.1018 | 0.19488
|  |  |  | 243.6 | 557770 |  |  | 82.1018 | 0.085955
|  |  |  | 573.9 | 352730 |  |  | 34.8493 | 0.012806
|  |  |  | 573.9 | 352730 |  |  | 34.8493 | 0.39026
|  |  |  | 573.9 | 352730 |  |  |  | 0.15996
|  |  |  | 231.15 | 448035 |  |  | 86.5239 | 0.36536
|  |  |  | 231.15 | 448035 |  |  | 86.5239 | 0.23508
|  |  |  | 231.15 | 448035 |  |  | 86.5239 | 0.10311
|  |  |  | 418.45 | 299765 |  |  |  | 0.017824
|  |  |  | 418.45 | 299765 |  |  | 47.7954 | 0.20758
|  |  |  | 565.35 | 370125 |  |  |  | 0.015219
|  |  |  | 565.35 | 370125 |  |  | 35.3763 | 0.21856

## cc (hidden)
y = a(MW) + b $millions
[9 empty] | a | 0.049975 | 49975
[9 empty] | b | 0.44885 | 448850
Per EPA
[9 empty] | a | 0.0497 | 49700
[9 empty] | b | 0.459 | 459000
SCR - EPA 1993 |  |  |  |  | x | y | x | y | Y | EPA's
|  |  |  | 1 | 0.135 | 0.29 | 3.661 | 0.63924 | 0.63305 | 0.64095
| Horizontal units |  |  | 2 | 0.1585 | 0.3082 | 4.2983 | 0.67935 | 0.66492 | 0.67263
|  | 160 | 5.9 | 3 | 0.346 | 0.418 | 9.3831 | 0.92138 | 0.91915 | 0.92534
|  | 20 | 0.7375 | 4 | 0.369 | 0.432 | 10.0068 | 0.95224 | 0.95034 | 0.95634
|  |  |  | 5 | 0.8085 | 0.7145 | 21.9254 | 1.5749 | 1.5463 | 1.5487
| Vertical Units |  |  | 6 | 0.984 | 0.813 | 26.6847 | 1.7921 | 1.7842 | 1.7852
|  | 9 | 4.083 | 7 | 1.286 | 0.9845 | 34.8746 | 2.1701 | 2.1937 | 2.1923
|  | 1 | 0.45367 | 8 | 1.487 | 1.087 | 40.3254 | 2.396 | 2.4663 | 2.4632
|  |  |  | 9 | 3.047 | 2.089 | 82.6305 | 4.6047 | 4.5815 | 4.5657
|  |  |  | 10 | 3.125 | 2.117 | 84.7458 | 4.6664 | 4.6873 | 4.6709
|  |  |  | 11 | 5.9 | 3.836 | 160 | 8.4555 | 8.45 | 8.411
12
HPWI - EPA 1993 |  |  |  |  | x | y | x | y
|  |  |  | 1 | 0.119 | 0.24 | 3.4776 | 0.39735 | 0.41426
| Horizontal units |  |  | 2 | 0.135 | 0.256 | 3.9452 | 0.42384 | 0.43077
|  | 160 | 5.475 | 3 | 0.748 | 0.665 | 21.8594 | 1.101 | 1.0631
|  | 20 | 0.68437 | 4 | 0.923 | 0.728 | 26.9735 | 1.2053 | 1.2437
|  |  |  | 5 | 2.833 | 2.392 | 82.7909 | 3.9603 | 3.214
| Vertical Units |  |  | 6 | 2.9235 | 1.568 | 85.4356 | 2.596 | 3.3074
|  | 5 | 3.02
|  | 1 | 0.604